## Slide 1: Micron-VE
External
NPI Applications Team
1 March, 2024
Rev 1 : 7 March, 2024

## Slide 2: Outline
-- Consolidated Flowsheet
- HFW pretreatment & concentration (RO1)
- HFW reject & LSR reject blending
- Jar Tests (SCE-1)
- RO2
- Jar Tests (SCE-2)
- CFRO
- Crystallizer
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 3
SCE-2
RO2
RO2 reject (7) ~ 32 L
93% rec
RO2 feed (6) ~ 450 L
SCE-2 supernatant (8)
CFRO
CFRO Feed (9)
SCE-1
Na Silicate
SCE-1 Feed (4)
SCE-1 supernatant (5)
LSR reject (3) ~ 225L
Mix tank 1
Stream | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
 | RO1 inlet | RO1 reject | LSR reject | SCE-1 feed | SCE-1 supernatant* | RO2 feed | RO2 reject | SCE-2 supernatant* | CFRO feed | CFRO reject
pH | 6.57 | 7.14 | 7.38 | 8.92 | 8.83 | 6.93 | 7.64 | 8.8 | 7.19 | 8.23
TDS, mg/L | 1373 | 7,154 | 428 | 5,098 | 4,410 | 5,188 | 66,800 | 62,928 | 64,520 | 169,440
Fe, mg/L | 0.112 | < 0.1 | 0.238 | <1 | 50.4 | <1 | 5.5 | 453 | 2.15 | 10.1
Silica, mg/L | 12.4 | 80.4 | 56 | 115 | 81.5 | 61.4 | 396 | 172 | 159 | 269.5
Na, mg/L | 484 | 3,168 | 158 | 2,250 | 1,937 | 2,265 | 29,580 | 26,900 | 23,560 | 61,720
F, mg/L | 358 | 1,689 | 197 | 1,341 | 1,189 | 1,527 | 17,359 | 18887 | 16,691 | 24,722
Cl, mg/L | 25.1 | 281 | 55.3 | 174 | 179 | 180 | 2,347 | 2,433 | 2,274 | 11,284
PO4, mg/L | 15.7 | 77.1 | <1 | 45.8 | 12.6 | 47.5 | 609 | 512 | 585 | 3,193
SO4, mg/L | 5.84 | 33.3 | 6.11 | 150 | 595 | 161 | 1,950 | 3,479 | 4,946 | 30,152
NO3, mg/L | 230 | 1,323 | 13.5 | 730 | 844 | 829 | 9,351 | 8,670 | 9637 | 24,761
CONSOLIDATED FLOWSHEET
* SCE-1&2 supernatant:- During the test, Fe2(SO4)3 at pH 8.5 was used, increasing pH above 9.3 helps with better silica removal and less Fe carryover (refer to SCE-2 Jar Test data).
RO1
RO1 reject (2) ~ 225L
86.7% rec
RO1 Inlet (1) ~ 1800L
HFW A1
HFW A2
UF1
NaF, NH4OH & H2SO4 dosed
NaOH, Fe2(SO4)3
H2SO4 (Feed pH 6.5-7.2)
H2SO4
(Feed pH 6.5 - 7.2)
NaOH, Fe2(SO4)3
UF2
RO2 pass 2
Pass 2 permeate
NaOH (pH 6.5-7.2)
CFRO reject (10)
62% rec
Crystallizer
NaF & Nitrate as salts
CFRO permeate
Notes: HFW Reject Fluoride=1658 mg/l. TDS is not consistent with slide 11 == TDS value changed to gravimetric!
Move label for Stream 4 to after the dosing point. It isn’t clear if that stream is before or after dosing == done
Is there an analysis for stream 4? == yes, SCE-1 feed
There is no stream between SBRO and SCE-2 == SBRO reject is to be treated using SCE-2
You should take out LSR process unit block, and just start with LSR reject stream. == done
Switch the Mix~450L as a tank. Then draw a line with chemical dosing == done
Draw stream 4 as a dotted line. To indicate it is not part of the normal process design == done
Show chemical addition as a different line == done
Should be using gravimetric TDS
Check all water parameters

## Slide 4: HFW Pretreatment & Concentration
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 5: HFW Feed & LSR reject
Objective:- HFW to be suitably pretreated and reconcentrated using RO.
3 samples received
HFW from A1,
HFW from A2 &
LSR reject
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 6: HFW Pretreatment
Blended equal volumes of HFW A1 and A2.
HFW Turbidity and TSS is high and needed pretreatment.
0.5-µm cartridge followed by 0.01 µm-UF were used for turbidity reduction.
UF is effective in turbidity removal (colloidal content in the sample is too fine to be removed by cartridge filter).
Parameter | HFW Feed (A1) | HFW Feed (A2)
pH | 2.94 | 3.23
TDS, mg/L | 756 | 14
SiO2 (mg/L) | 17.4 | 8.19
Na (mg/L) | 187 | 7.67
F (mg/L) | 462 | 130
Cl (mg/L) | 23.2 | 13.8
PO4 (mg/L) | 28.4 | 4.21
SO4 (mg/L) | 4.76 | 7.41
NO3 (mg/L) | 742 | 4.34
NH4 (mg/L) | 10 | 10.4
Turbidity (NTU) | 255 | 64.3
TSS (mg/L) | 81 | 16
0.5-µm cartridge
UF

## Slide 7: RO1
Objective:- HFW feed stream is to be concentrated using the pressurized RO setup
Feed pressure: upto 1000 psi (69 bar); Flow ~ 6 lpm; Concentrated ~ 1800 L of feed into ~ 250 L
( ~ 86% recovery; 7x concentration)
Pressure vessel
High-pressure pump
Parameter | RO1 Inlet | RO1 Reject
pH | 6.57 | 7.14
TDS, mg/L | 1373 | 7154
SiO2 (mg/L) | 12.4 | 80.4
Na (mg/L) | 484 | 3168
F (mg/L) | 358 | 1689
Cl (mg/L) | 25.1 | 281
PO4 (mg/L) | 15.7 | 77.1
SO4 (mg/L) | 5.84 | 33.3
NO3 (mg/L) | 230 | 1323
NH4 (mg/L) | 7.2 | 37
Notes: This is HFW + LSR stream

## Slide 8: HFW reject and LSR reject Blending
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 9: Mixing Tank blending
Blended the HFW reject with LSR reject suitably to obtain ~ 1366 ppm Fluoride & NH4 ~ 109 ppm as per design.
Parameter | HFW reject | LSR Reject | Blend | Spike NaF+NH4OH to match design => SBRO feed
pH | 7.14 | 7.38 | 7.1 | 6.93
TDS, mg/L | 7154 | 428 | 3878 | 5188
SiO2 (mg/L) | 80.4 | 56 | 72.7 | 61.4
Na (mg/L) | 3168 | 158 | 1722 | 2265
F (mg/L) | 1689 | 197 | 963 ~1365 (design) | 1527
Cl (mg/L) | 281 | 55.3 | 164 | 180
PO4 (mg/L) | 77.1 | <1 | 42.4 | 47.5
SO4 (mg/L) | 33.3 | 6.11 | 19 | 161
NO3 (mg/L) | 1323 | 13.5 | 649 | 829
NH4 (mg/L) | 37 | 111 | 53 ~ 109 (design) | 80

## Slide 10: SCE -1 (Jar Tests)
Conducted offline
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 11: Jar Test Objective
To conduct Jar tests to determine optimal SiO2 reduction (≤20 mg/L for SCE-1) and (≤30 mg/L for SCE-2) to meet downstream process quality requirements.
SCE-1 details:
Feed: Blended LSR & HFW RO reject streams; with SiO2 adjusted to 140 mg/L (as per design requirement)
Coagulant: FeCl3 (pH8.5-9.0);
Fe2(SO4)3 (pH8.5-9.0)
(pH > 9.3) (preferable range) FeSO4 (pH8.5-9.0); MgCl2 (pH 10.5-11.0); MgSO4 (pH 10.5-11.0)
Polymer: 1 ppm
Mixing Regime
Coagulant mixing: 200-rpm for 1 min  100-rpm for 30 min
Polymer mixing: 30-rpm for 15 min
Settling: 0-rpm for 30 min

## Slide 12: SCE-1 Jar Tests Summary
Coagulant | Fe2(SO4)3 | FeCl3 | MgSO4 | MgCl2 | FeSO4
Dosages tested, mg/L | 750; 1,000; 1,250; 1,505; 2,005 | 610; 815; 1,220 | 1,040; 1,390; 1,735 | 825; 1,100; 1,370 | 570; 760; 950; 1,140; 1,525
Total Silica, mg/L Feed Supernatant | 115 48 - 137 | 115 13.8 - 46 | 125 35.5 - 75.1 | 125 45.1 - 78.7 | 120.9 13.0 – 42.4
Best Cases | 58.3% reduction 2,005 mg/L (pH8.8) => based on SCE-2 trials, pH > 9.3 are effective | 88.0% reduction 1,220 mg/L (pH8.8) | 71.6% reduction 1,735 mg/L (pH11.0) | 63.9% reduction 1,370 mg/L (pH11.0) | 89.2% reduction 1,525 mg/L (pH8.8)
Remarks | Unsatisfactory performance; difficulty in solubilizing coagulant, forming slurry < use liquid coagulant instead of powder > | Better performance, but added Cl to supernatant | Unsatisfactory performance, didn’t pursue further | Unsatisfactory performance, didn’t pursue further | Best performance, forming clearest supernatants
FeSO4 is picked as the most suitable coagulant/ Fe2(SO4)3 may be tried at higher pH.

## Slide 13: SCE-1 Jar Test with FeSO4 solution
After polymer addition
After 30-min settling
Notes: Fix title == done

## Slide 14: SCE-1 Jar Test with FeSO4 solution <analysis>
 | 1) SCE-1 Feed | 2) FeSO4 570mg/L | 3) FeSO4 760mg/L | 4) FeSO4 950mg/L | 5) FeSO4 1,140mg/L | 6) FeSO4 1,525mg/L
pH | 8.72 | 8.49 | 8.53 | 8.48 | 8.46 | 8.2
Total Silica, mg/L | 120.9 | 42.4 | 26.1 | 22.7 | 16.4 | 13.0
Dissolved Silica, mg/L | 101.5 | 34.3 | 24.8 | 19.5 | 14.3 | 10.2
Conductivity, μS/cm | 8,920 | 8,990 | 9,660 | 9,860 | 10,060 | 10,240
TDS, mg/L | 4,876 | 5,137 | 5,335 | 5,408 | 5,523 | 5,716
Na, mg/L | 2,227 | 2,529 | 2,446 | 2,284 | 2,594 | 2,616
Fe, mg/L | <1 | 6.77 | <1 | 2.16 | 5.25 | 9.77
Cl, mg/L | 174.25 | 172.78 | 172.15 | 173.5 | 372.14 | 173.34
SO4, mg/L | 150.54 | 515.11 | 621.56 | 756.3 | 854.69 | 1,113.5
Based on supernatant clarity, silica removal (upto~ 20 ppm), and residual Fe, FeSO4 760 mg/L is chosen.
Tackling Fe carryover in downstream processes - (if Fe > 1 ppm, filter through CF at pH ≥8.8)
Notes: SCE Control -> Feed

## Slide 15: RO2
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 16: Experimental Setup
Objective:- (HFW+LSR) reject stream feed stream is to be concentrated using the pressurized RO setup
  Feed pressure: upto 1000 psi (69 bar)
  Flow ~ 6 lpm
  Concentrated ~ 450 L of feed into ~ 32 L ( ~ 93% recovery; 14x concentration)
Pressure vessel
High-pressure pump
  RO2 Second pass
  Feed pressure: upto 10 bar
  Flow ~ 3.5 lpm

## Slide 17: RO2 – First & Second Pass - Analysis
RO pass 1 and pass 2 permeate results are satisfactory.
Parameter | RO2 feed | RO2 reject (~ 93% recovery) | RO2 permeate (1st pass) | RO2 permeate (2nd pass)
pH | 6.93 | 7.64 | 7.23 | 6.47
TDS, mg/L | 5188 | 66800 | 40 | 3
SiO2 (mg/L) | 61.4 | 396 | < 0.2 | < 0.2
Na (mg/L) | 2265 | 29580 | 6.4 | 1.13
F (mg/L) | 1527 | 17359 | 4.18 | 0.412
Cl (mg/L) | 180 | 2347 | 1.45 | 1.17
PO4 (mg/L) | 47.5 | 609 | < 0.1 | < 0.1
SO4 (mg/L) | 161 | 1950 | 0.296 | 0.238
NO3 (mg/L) | 829 | 9351 | 7.32 | 0.199
NH4 (mg/L) | 80 | 1010 | 2.1 | < 0.4
Pass 2 Feed
Pass 2 Permeate
RO2 feed
RO2 reject
RO2 permeate

## Slide 18: SCE -2 (Jar Tests)
FeSO4 (High sludge volume)
Fe2(SO4)3 (Lower sludge volume)
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 19: SCE-2–FeSO4
After polymer addition
After 30-min settling
FeSO4 is effective in silica removal, but the amount of sludge volume is high!

## Slide 20: SCE-2 – FeSO4
 | 1) SCE-2 Feed | FeSO4* 2175 mg/L | 2) FeSO4 2,720mg/L | 3) FeSO4 3,260mg/L | 4) FeSO4 4,350mg/L
pH | 8.07 | 8.49 | 8.19 | 8.04 | 7.99
Total Silica, mg/L | 340 | 75.1 | 21.8 | 26.3 | 24.6
Dissolved Silica, mg/L | 186 | 82.7 | 16.6 | 22.2 | 13.7
Conductivity, μS/cm | 68,300 | 62,500 | 68,400 | 68,400 | 68,500
TDS, mg/L | 32410 | 24720 | 36130 | 37480 | 39180
Na, mg/L | 23,184 | 21710 | 29,351 | 28,080 | 25,889
Fe, mg/L | 2.04 | 35.1 | 53.1 | 78.8 | 60.3
Cl, mg/L | 2,253 | 2977 | 2,213 | 2,180 | 2,184
SO4, mg/L | 2,548 | 3925 | 5,738 | 6,657 | 7,744
W, mg/L | 131 | xx | 123 | 109 | 60
Based on design limit of (≤30 mg/L silica for SCE-2); 2720 mg/L FeSO4 could be chosen.
Tackling Fe carryover in downstream processes? => (Maintain supernatant pH> 8.8, filter through CF/UF to bring down Fe levels)
How about ‘W’ removal?
Its removal rate is 50% with higher FeSO4 dosage, but not practical due to high sludge volume.
*Note:- This test was performed for a similar water source in a separate experiment.
Notes: Include 1 lower result - included

## Slide 21: SCE-2 – FeSO4 vs Fe2(SO4)3 vs MgSO4

## Slide 22: SCE-2 – FeSO4, vs Fe2(SO4)3 vs MgSO4
FeSO4 is effective in silica removal, but the amount of sludge volume is high!
Based on design limit of (≤30 mg/L silica for SCE-2); Fe2(SO4)3 could be the next best option (@ pH >9.3) for effective silica removal.
For Fe carryover, use UF2 to filter before sending the stream to CFRO.
Tungsten removal is not achievable during the jar test.
 | SCE-2 Feed | FeSO4 2,175mg/L | FeSO4 2,720 mg/L | Fe2(SO4)3 3,580mg/L | MgSO4 5,940 mg/L | MgSO4 9,905 mg/L
pH | 8.36​ | 8.9​ | 8.93​ | 9.62​ | 11.64​ | 11.84​
Total Silica, mg/L | ~240 | 25.5​ | 23.3​ | 38.5​ | 278​ | 255​
Dissolved Silica, mg/L | ~70 | 20.9​ | 17.3​ | 30.3​ | 250​ | 214​
Conductivity, μS/cm | 63,500​ | 63,800​ | 64,000​ | 62,000​ | 59,600​ | 54,000​
TDS, mg/L | 53,360​ | 55,200​ | 54,510​ | 47,720 | 41,600 | 44,370
Na, mg/L | 24,450​ | 20,480​ | 22,490​ | 18,870​ | 20,430​ | 20,500​
Fe, mg/L | 3.91​ | 24.2​ | 30​ | 8.46​ | <1​ | <1​
Cl, mg/L | 2,189​ | 2,509​ | 2,067​ | 2,551​ | 3,282​ | 2,279​
SO4, mg/L | 2,594​ | 4,567​ | 4,420​ | 4,205​ | 8,934​ | 10,804​
W, mg/L | 148 | 150 | 140 | 142 | 147 | 141

## Slide 23: CFRO
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 24: Experimental Set-Up
RO reject is treated via SCE-2 UF  pH adj (6.5-7.2 range for better ammonia rejection) and fed into CFRO for brine concentration.
Custom, proprietary membranes were employed in the CFRO module.
Objective: Further concentration of RO reject to ~180,000 mg/L TDS

## Slide 25: Analysis results
Feed RI ~ 1.3405 ~ 64,520 ppm TDS
Reject RI ~ 1.3534 ~ 169,440 ppm TDS
Final recovery based on TDS ~ ((169440/64540)-1)/(169440/64520) ~ 61.9%
*Note: CFRO feed silica is high, to optimize silica removal (using Jar tests)
Parameter | CFRO feed | CFRO reject (~ 62% recovery)
pH | 7.19 | 8.23
TDS, mg/L | 64520 | 169440
SiO2 (mg/L) | 159 | 269.5
Na (mg/L) | 23560 | 61720
F (mg/L) | 16691 | 24722
Cl (mg/L) | 2274 | 11284
PO4 (mg/L) | 585 | 3193
SO4 (mg/L) | 7263 | 30152
NO3 (mg/L) | 9637 | 24761
NH4 (mg/L) | 472.2 | 5,580
Notes: Future works include optimizing silica removal

## Slide 26: Bar charts
Na, F and NO3 are the main constituents in RO2 feed.
In CFRO feed, excess sulphate was added to match design (hence sulphate% has increased).
Chart: RO2 feed
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten
SBRO feed | 0.29433 | 0.031033 | 0.011835 | 0.43658 | 0.034695 | 0.01542 | 0.0091557 | 0.15979 | 0.032382
Chart: RO2 reject
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten
SBRO reject | 0.25987 | 0.029192 | 0.0059281 | 0.44281 | 0.035135 | 0.01512 | 0.0091168 | 0.13999 | 0.035943
Chart: CFRO feed
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten
CFRO feed | 0.25869 | 0.11257 | 0.0024644 | 0.36516 | 0.035245 | 0.0073187 | 0.009067 | 0.14936 | 0.031153
Chart: CFRO reject
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten
CFRO Reject | 0.1459 | 0.17795 | 0.0015906 | 0.36426 | 0.066596 | 0.032932 | 0.018844 | 0.14613 | 0.026853
Note: Salt solubility in water at 300 C
Salt solubility in water at 100 C
Notes: This bar chart shows %of ions against total ion composition, not the concentration in %.
Most of them add upto 100%

## Slide 27: Crystallizer
Notes: -Experimental Results, Model Data, Learnings (The bulk of the presentation)

## Slide 28: Procedure
CFRO reject
Chilling – to precipitate Na2SO4 cooling crystallization

## Slide 29: Crystallizer salt composition
Main constituents are:- Na, F, SO4, NO3
For separation of fluoride salts from sulphate, Nanofiltration could be used.
Chart: CFRO rej supernatant => crystallizer powder
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten | B-boron
Crystalliser Supernatant (Individual/Total ions) | 0.19235 | 0.18011 | 0.040274 | 0.34324 | 0.063794 | 0.00019332 | 0.0082911 | 0.12222 | 0.025238 | 0.0036945
IC-ICP analysis
Note: The detectable element range of XRF starts from element F; for XRD is from element B, hence NO3 ion visible in XRD does not show up as final “N%” in XRF.
XRF
XRD-XRF analysis
Notes: Better name == crystallizer salt composition

## Slide 30: CFRO Precipitate Composition (Sodium Sulphate rich?)
This precipitate was formed even before chilling, probably due to NaF precipitation.
Precipitate is Fluoride- and tungsten-rich, instead of sulphate-rich! (Perhaps, chilling could have helped to precipitate out some amount of sulphate, but most of it remained in the supernatant!)
Since this precipitate is fluoride-rich, this fraction also could be sent to the crystallizer directly to obtain NaF powder.
Any concerns over W-in the final powder?
Chart: CFRO rej precipitate
| F | SO4 | SiO2 | Na | Cl | NH4 | PO4 | NO3 | W-tungsten | B-boron | K-potassium | Tl-Thallium
Crystalliser precipitate(Individual/Total ions) | 0.32812 | 0.063369 | 0.0060333 | 0.39489 | 0.017901 | 0.0090314 | 0.0062959 | 0.053989 | 0.12187 | 0.0017004 | 0.00068122 | 0.001743
IC-ICP analysis
Notes: Take out the co-ion effect slide

## Slide 31: Crystallizer Step – Future works
For selective removal of NaF from other salts, CFRO reject (supernatant) could be post-treated using NF, to remove sulphate ions in the NF reject.
NF permeate (with higher concentration of NaF and NaNO3) could be crystallized further!
CFRO rej precipitate (rich in NaF and tungstate) in slurry form could be sent to crystallizer directly!
CFRO
CFRO reject (10)
62% rec
CFRO Feed (9)
SO42- rich reject
Crystallizer
NaF & Nitrate
Nanofiltration
F- and NO3- rich permeate
CFRO rej precipitate
Notes: Future Works