## Slide 1
Sustainable Solutions for Complex Waters
IPA Removal System Options
Siva

## Slide 2
Influent Wastewater Characteristics (4 m3/hr)
Treated Water: ~3.88 m3/hr (IPA <10 ppm)
IPA recovery: ~ 0.12 m3/hr (>85% purity )
Effluent
Characteristics
Case study

## Slide 3
IPA/Water mixtures freezing point curve
Micron WW stream contains 15371 mg/l of IPA
At low temperatures concentrated IPA will have higher density
Chart: IPA density variations with temperature
Chart: Freezing point variations with IPA concentration
| 0 | 8 | 17 | 26 | 34 | 44 | 54 | 65 | 76 | 88 | 100
Freezing point (C) | 0 | -4 | -7 | -15 | -18 | -21 | -23 | -29 | -37 | -57 | -73
ICE density 0.92
Notes: The increase in volume of ice is about 9%. This increase causes enough force to break most rigid containers. This is the same force, repeated on a daily basis, that creates "pot holes" in the roads in the winter time.

## Slide 4
Flow Scheme Option 1 – Low temperature crystallization
LT Reactor – Low Temperature crystallization (-4C)*
AC - Alcohol Concentrator (RO)
Polishing – RO and wash with permeate
IPA – Isopropyl Alcohol
UF
Polishing
AC
LT Reactor
Recovered Water
Influent
Recovered IPA
*Theoretically -4C is enough, planning to perform freezing tests to validate the temperature.
COD/TOC analyzer

## Slide 5
Process Description – Single/Double stage IPA Con.
Pre-cool the WW stream using plate frame/shell & tube HXs to a desired temperature.
Reactor should maintain the temperature below the theoretical value (-4C)
Based on the density the IPA and Ice will separate. If required, use the centrifuge for the solid/liquid separation.
IPA can be further concentrated using the 2nd stage reactor with low temperature crystallization or using the RO/CFRO membranes.
Ice can be crushed in a crusher before it is going to heat exchange with the incoming WW stream.
Wash water can be used for the polishing/washing of ice to remove the surface impurities.
Chillers and centrifuges are available for the given temperature.

## Slide 6
Flow Scheme Option 2 – Alternative crystallization
Reactor – Chemical addition to extract IPA
AC - Alcohol Concentrator (Distillation Column/Stripper)
Polishing – RO
IPA – Isopropyl Alcohol
UF
Polishing
AC
Reactor
Recovered Water
Influent
Recovered IPA
Reusing solvent

## Slide 7: Micron IPA WW - Freezer study
Performed the freezer study using the Micron IPA WW.
Test procedure:
  Collected known volume of (100 ml) WW sample
  Kept inside the lab freezer overnight.
  Observed the Ice formation along with Concentrated IPA in the liquid form.
  Collected concentrated IPA in a separate vial.
  Washed the ICE and collected the washed liquid.
  Kept ICE for melting.
  Analysed sample for the COD, TDS.
Visual observation shows that good separation between two layers.

## Slide 8
Lab Freezer study test 1
ICE + Con. IPA
WW sample
ICE + Con. IPA
Concentrated IPA > 12.5%
Concentrated IPA COD- 279000 mg/l
Melted ICE: TDS – 172 PPM
Melted ICE IPA > 10 PPM
Inlet IPA – 1.5%
Inlet COD- 50000 mg/l

## Slide 9
Lab Freezer study test 2
ICE + Con. IPA
WW sample
ICE + Con.IPA
Concentrated IPA >14.8%
Concentrated IPA COD - 320000 PPM
Melted ICE: TDS – 170 PPM
Melted ICE IPA > 10 PPM
Inlet IPA – 1.5%
Inlet COD- 50000 mg/l

## Slide 10: THANK YOU