## Slide 1: Pilot Study Update
Client: Exyte
Location: Singapore
Date : 24 Jan 2024

## Slide 2: Discussion points
First round of sample collection started on 23rd Jan 24, will end on 28 Jan 24
Micron LSR HFW Sampling Log.xlsx

## Slide 3: HFW and LSR sampling points – Run 1
Sampling points | Volume (L) | Total volume for each collection (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 70 | 100 | 10 | 1000 (1m3)
HFW Gravity Drain A2 | 30 |  |  | 
HFW Gravity Drain Chem Room | 2* | 2 |  | 20
HFW Gravity Drain Corrosive gas room | 2* | 2 |  | 
 |  |  |  | 20
LSR A2 |  |  |  | 
LSR A2 transfer pump | 100 | 100 | 10 | 1000 (1m3)
Ratio HFW A1: A2= 7:3
*Collect in two separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 4: HFW and LSR sampling points – Run 2
Sampling points | Volume (L) | Total volume (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 280 | 400 | 10 | 4000 (4m3)
HFW Gravity Drain A2 | 120 |  |  | 
HFW Gravity Drain Chem Room | 8* | 8 |  | 80
HFW Gravity Drain Corrosive gas room | 8* | 8 |  | 
 |  |  |  | 80
LSR A2 |  |  |  | 
LSR A2 transfer pump | 400 | 400 | 10 | 4000 (4m3)
*Collect in 8x separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 5: Sampling plan

## Slide 6: Sampling plan for HFW A1 and A2
7x 10 L
3x 10 L
2 collections each day for 5 days
1 collection per shift
18 – 22 Jan 2024

## Slide 7: Sampling plan for HFW Chem Room and Gas Room
2 L
2 L

## Slide 8: Sampling plan for LSR A2
5x 20 L
2 collections each day for 5 days
1 collection per shift
18 – 22 Jan 2024

## Slide 9: Pilot setup – membrane and pressure vessel
BW30 PRO-4040

## Slide 10
Feed tank
BW30 PRO-4040
High pressure pump
Booster pump
Cartridge filter

## Slide 11: Schedule
Event | Description | Date
01 | Pilot Readiness | 25-Jan
02 | Sample Collection at Site | 18-Jan to 25-Jan 23 Jan – 2 Feb
03 | Micron/Exyte witness | 01-Feb (?) - to be confirmed by Kristine and get back tomorrow
04 | Pilot Operation | 26-Jan to 08-Feb
05 | Report Preparation | 09-Feb to 22-Feb
06 | Draft Submission Review | 23-Feb to 07-Mar
07 | Final Report Submission | 08-Mar to 15-Mar