## Slide 1: Jar testing Procedure
To each testing jar, pour in 1L of wastewater sample
To each jar, dose in 4000 - 7000 mg/L of Ca(OH)2 and rapid mix for 30s
Slow mix for 30 min, measure pH every 15 min
Dose 1mg/L for each of the AN905 polymer (anionic) in each jar and further slower mix (30 rpm) for 30 min. Measure pH every 15 min
Stop mixing and leave the solids to settle over 60 min
Observe sludge settling and measure sludge height every 15 min (if applicable)
Measure turbidity of supernatant and collect the sludge
For the jar with the lowest supernatant turbidity reading, filter out the supernatant through 0.45 um filter and send for analysis and collect the sludge generated
For the sludge collected, filter out using 1.5 µm filter. Collect the sludge, dry sample for XRF analysis.

## Slide 2: Water Analysis of HFW Pump Discharge
Elements | Concentration based on in-house measurement (ppm)
F | 455.8
Cl | 251.3
SO4 | 30.6
I | 4.1
NO3 | 61.6
NH3 | 56
Al | 10.9
B | 0.778
Ca | 4.09
Fe | 0.129
Mg | 0.688
Ni | 0.52
K | 1.5
SiO2 | 55
Na | 308
Elements | Characteristics based on in-house measurements | Units
pH | 3.42 | -
Conductivity | 1794 | µS/cm
Colour (True) | 350 | Pt/Co
TDS | 956.9 | mg/l
Turbidity | 154 | NTU
TSS | 83 | mg/l
TOC | 26.71 | mg/l
COD | 277 | O2 mg/l
Total Chlorine | 1.16 | mg/l

## Slide 3: Scheme 1: Jar testing of HFW pump discharge with Lime
HFW Pump Discharge solution in different jars
HFW Pump Discharge with added lime at different dosages (4000, 5000, 6000 ppm)
Solution with added flocculant (Flopam AN 905 SH). Precipitates clumped and settled after the addition of flocculant.

## Slide 4: Treatment 1: Jar testing of HFW pump discharge with Lime
Jar | Lime dosage (ppm) | pH |  | 
 |  | t = 0 min | t = 15 min | t = 30 min
1 | 4000 | 3.65 | 12.49 | 12.46
2 | 5000 | 3.65 | 12.49 | 12.53
3 | 6000 | 3.69 | 12.46 | 12.56
Chemical precipitation with Ca(OH)2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | Lime dosage (ppm) | pH |  |  | Polymer used
 |  | t = 0 min | t = 15 min | t = 30 min | 
1 | 4000 | 12.46 | 12.48 | 12.49 | Flopam AN 905 SH
2 | 5000 | 12.53 | 12.49 | 12.44 | Flopam AN 905 SH
3 | 6000 | 12.56 | 12.52 | 12.44 | Flopam AN 905 SH

## Slide 5: Treatment 1: Jar testing of HFW pump discharge with Lime
Elements | Concentration, in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3
pH | 3.42 | 12.49 | 12.44 | 12.44
Turbidity | 154 NTU | 13.1 NTU | 13.5 NTU | 15.8 NTU
F | 455.8 | 8.98 | 8.68 | 8.55
Cl | 251.3 | 46.6 | 46.5 | 46.4
SO4 | 30.6 | 7.37 | 8.09 | 9.36
NO3 | 61.6 | 58.2 | 58.1 | 58.8
Al | 10.9 | <0.1 | <0.1 | <0.1
Ba | <0.1 | 0.118 | 0.128 | 0.13
B | 0.778 | 1.53 | 1.55 | 1.60
Ca | 4.09 | 711 | 756 | 757
Fe | 0.129 | <0.1 | <0.1 | <0.1
Mg | 0.688 | <0.1 | <0.1 | <0.1
Ni | 0.52 | <0.1 | <0.1 | <0.1
K | 1.5 | 12.7 | 13.1 | 13.5
SiO2 | 55 | <0.1 | 0.227 | 0.227
Na | 308 | 334 | 358 | 344
Sr | <0.1 | 0.445 | 0.509 | 0.551

## Slide 6: Treatment 1: Jar testing of HFW pump discharge with Lime
Jar | Lime dosage (ppm) | Weight of Wet Sludge (g) | Weight of Dry Sludge (g) | Moisture Content of Wet Sludge
1 | 4000 | 10.627 | 3.010 | 71.7%
2 | 5000 | 12.742 | 3.962 | 68.9%
3 | 6000 | 14.892 | 4.909 | 67.0%
Sludge collected from vacuum filtration and dried in 80C oven.

## Slide 7: Scheme 2A: Jar testing of HFW pump discharge with CaCl2 and NaOH pH adjustment
HFW Pump Discharge solution in Jar 1, 2, and 3
HFW Pump Discharge adjusted pH to 7-8 with NaOH, added CaCl2 at different dosages (2500, 3000, 4000 ppm),
Solution with added flocculant (Flopam AN 905 SH). Solution stays turbid even with addition of flocculant, and did not settle down

## Slide 8: Scheme 2A: Jar testing of HFW pump discharge with CaCl2 and NaOH pH adjustment
Jar | CaCl2 dosage (ppm) | NaOH dosage (ppm) | pH | pH |  | 
 |  |  | Initial pH adjustment | t = 0 min | t = 15 min | t = 30 min
1 | 2500 | 450 | 7.96 | 6.4 | 6.4 | 6.4
2 | 3000 | 440 | 7.5 | 6.5 | 6.4 | 6.6
3 | 4000 | 450 | 7.44 | 6.4 | 6.4 | 6.5
Chemical precipitation with pH adjustment, then CaCl2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | CaCl2 dosage (ppm) | NaOH dosage (ppm) | pH |  |  | Polymer used
 |  |  | t = 0 min | t = 15 min | t = 30 min | 
1 | 4000 | 450 | 6.4 | 6.5 | 6.5 | Flopam AN 905 SH
2 | 5000 | 440 | 6.6 | 6.6 | 6.6 | Flopam AN 905 SH
3 | 6000 | 450 | 6.5 | 6.5 | 6.5 | Flopam AN 905 SH

## Slide 9: Scheme 2A: Jar testing of HFW pump discharge with CaCl2 and NaOH pH adjustment
Elements | Concentration, in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3
pH | 3.42 | 6.5 | 6.6 | 6.5
Turbidity | 154 NTU | 123 NTU | 131 NTU | 209 NTU
F | 455.8 | 11.3 | 11.0 | 12.8
Cl | 251.3 | 1,446 | 1,489 | 1,298
SO4 | 30.6 | 4.31 | 4.54 | 4.95
NO3 | 61.6 | 57.3 | 58.2 | 57.1
Al | 10.9 | <0.1 | <0.1 | <0.1
Ba | <0.1 | 0.204 | 0.111 | 0.109
B | 0.778 | 1.51 | 1.53 | 1.58
Ca | 4.09 | 405 | 423 | 325
Fe | 0.129 | <0.1 | <0.1 | <0.1
Mg | 0.688 | 1.72 | 1.81 | 1.47
Ni | 0.52 | <0.1 | <0.1 | <0.1
K | 1.5 | 11.0 | 4.77 | 8.38
SiO2 | 55 | 44.7 | 45.3 | 44.8
Na | 308 | 548 | 544 | 569
Sr | <0.1 | 0.344 | 0.366 | 0.284

## Slide 10: Scheme 2A: Jar testing of HFW pump discharge with CaCl2 and NaOH pH adjustment
Jar | CaCl2 dosage (ppm) | NaOH dosage (ppm) | Weight of Wet Sludge (g) | Weight of Dry Sludge (g) | Moisture Content of Wet Sludge
1 | 2500 | 450 | 6.108 | Sludge was not dried for this testing, as there is very little to be obtained. | 
2 | 3000 | 440 | 4.003 |  | 
3 | 4000 | 450 | 4.141 |  | 
Sludge collected from vacuum filtration, discarded as no solids are visible.

## Slide 11: Scheme 2B: Jar testing of treated water in 2A with CaCl2 (2 step precipitation)
Jar 1 and 2 filled with 500mL of HFW Supernatant treated with 2500 ppm and 3000 ppm CaCl2
Additional 1000 ppm of CaCl2 was added to both jars for 2nd step precipitation.
Solution with added flocculant (Flopam AN 905 SH). Precipitates clumped and settled after the addition of flocculant.

## Slide 12: Scheme 2B: Jar testing of treated water in 2A with CaCl2 (2 step precipitation)
Jar | CaCl2 dosage (ppm) | NaOH dosage (ppm) | pH |  | 
 |  |  | t = 0 min | t = 15 min | t = 30 min
1 | 2500 + 1000 | 450 | 7.3 | 7.29 | 7.31
2 | 3000 + 1000 | 440 | 7.3 | 7.29 | 7.31
Chemical precipitation with CaCl2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | CaCl2 dosage (ppm) | NaOH dosage (ppm) | pH |  |  | Polymer used
 |  |  | t = 0 min | t = 15 min | t = 30 min | 
1 | 2500 + 1000 | 450 | 7.31 | 7.34 | 7.32 | Flopam AN 905 SH
2 | 3000 + 1000 | 440 | 7.31 | 7.19 | 7.18 | Flopam AN 905 SH

## Slide 13: Scheme 2B: Jar testing of treated water in 2A with CaCl2 (2 step precipitation)
Elements | Supernatant quality for Jar 1 (1st step) | Supernatant quality for Jar 2 (1st step) | Supernatant quality for Jar 1 (2nd Step) | Supernatant quality for Jar 2 (2nd Step)
pH | 6.5 | 6.6 | 7.32 | 7.18
Turbidity | 123 NTU | 131 NTU | 1.84 NTU | 4.11 NTU
F | 11.3 | 11.0 | 6.39 | 6.82
Cl | 1,446 | 1,489 | 2,056 | 2,005
SO4 | 4.31 | 4.54 | 5.98 | 5.08
NO3 | 57.3 | 58.2 | 53.7 | 53.2
Al | <0.1 | <0.1 | <0.1 | <0.1
Ba | 0.204 | 0.111 | 0.45 | 0.351
B | 1.51 | 1.53 | 1.57 | 1.60
Ca | 405 | 423 | 728 | 753
Fe | <0.1 | <0.1 | <0.1 | <0.1
Mg | 1.72 | 1.81 | 2.79 | 2.54
Ni | <0.1 | <0.1 | <0.1 | <0.1
K | 11.0 | 4.77 | 11.0 | 12.8
SiO2 | 44.7 | 45.3 | 45.0 | 43.7
Na | 548 | 544 | 567 | 541
Sr | 0.344 | 0.366 | 0.500 | 0.534
Zn | <0.1 | <0.1 | 0.119 | 0.114
Notes: Omitted strontium and barium

## Slide 14: Scheme 2B: Jar testing of treated water in 2A with CaCl2 (2 step precipitation)
Jar | CaCl2 dosage (ppm) | Lime dosage (ppm) | Weight of Wet Sludge (g) | Weight of Dry Sludge (g) | Moisture Content of Wet Sludge
1 | 2500 + 1000 | 450 | 2.143 | 0.026 | 98.8%
2 | 3000 + 1000 | 440 | 2.28 | 0.026 | 98.9%
Sludge collected from vacuum filtration and dried in 80C oven.

## Slide 15: Scheme 3: Jar testing of HFW pump discharge with CaCl2 and lime pH adjustment
HFW Pump Discharge solution in Jar 1, 2, and 3
HFW Pump Discharge adjusted pH to >8 with Lime, added CaCl2 at different dosages (1500, 2000, 2500 ppm)
Solution with added flocculant (Flopam AN 905 SH). Precipitates clumped and settled after the addition of flocculant.

## Slide 16: Scheme 3: Jar testing of HFW pump discharge with CaCl2 and lime pH adjustment
Jar | CaCl2 dosage (ppm) | Lime dosage (ppm) | pH | pH |  | 
 |  |  | Initial pH adjustment | t = 0 min | t = 15 min | t = 30 min
1 | 1500 | 550 | 8.66 | 8.19 | 8.92 | 9.1
2 | 2000 | 600 | 9.04 | 8.59 | 9.15 | 9.3
3 | 2500 | 800 | 10.43 | 10.02 | 10.41 | 10.52
Chemical precipitation with pH adjustment, then CaCl2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | CaCl2 dosage (ppm) | Lime dosage (ppm) | pH |  |  | Polymer used
 |  |  | t = 0 min | t = 15 min | t = 30 min | 
1 | 1500 | 550 | 9.1 | 9.1 | 9.08 | Flopam AN 905 SH
2 | 2000 | 600 | 9.3 | 9.29 | 9.28 | Flopam AN 905 SH
3 | 2500 | 800 | 10.52 | 10.49 | 10.47 | Flopam AN 905 SH

## Slide 17: Scheme 3: Jar testing of HFW pump discharge with CaCl2 and lime pH adjustment
Elements | Concentration, in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3
pH | 3.42 | 9.08 | 9.28 | 10.47
Turbidity | 154 NTU | 3.64 NTU | 9.31 NTU | 15.9 NTU
F | 455.8 | 18.6 | 11.2 | 10.4
Cl | 251.3 | 888 | 1,160 | 1,458
SO4 | 30.6 | 6.86 | 7.03 | 10.2
NO3 | 61.6 | 58.3 | 58.8 | 57.0
Al | 10.9 | 0.195 | 0.313 | 2.46
Ba | <0.1 | 0.103 | 0.107 | 0.111
B | 0.778 | 1.29 | 1.13 | 1.03
Ca | 4.09 | 294 | 454 | 677
Fe | 0.129 | <0.1 | <0.1 | <0.1
Mg | 0.688 | 1.61 | 1.92 | 2.15
Ni | 0.52 | <0.1 | <0.1 | <0.1
K | 1.5 | 8.31 | 5.78 | 14.0
SiO2 | 55 | 13.3 | 4.17 | 0.873
Na | 308 | 294 | 292 | 293
Sr | <0.1 | 0.269 | 0.389 | 0.491
Notes: Omitted strontium and barium

## Slide 18: Scheme 3: Jar testing of HFW pump discharge with CaCl2 and lime pH adjustment
Jar | CaCl2 dosage (ppm) | Lime dosage (ppm) | Weight of Wet Sludge (g) | Weight of Dry Sludge (g) | Moisture Content of Wet Sludge
1 | 1500 | 550 | 4.484 | 1.223 | 72.7%
2 | 2000 | 600 | 5.575 | 2.15 | 61.4%
3 | 2500 | 800 | 4.754 | 1.346 | 71.7%
Sludge collected from vacuum filtration and dried in 80C oven.

## Slide 19: Summary
Fluoride level was effectively reduced to <10 ppm by Scheme 1 (Lime dosage: 4000 ppm) and Scheme 2a and 2b (2-step chemical precipitation with 2500ppm and 1000ppm of CaCl2 for 1st step and 2nd step respectively).
Scheme 3 (CaCl2 dosing and lime dosing for pH adjustment) was found less effective in removing fluoride in HFW. The fluoride level remain slightly above 10 ppm with maximum dosage of 2500 ppm CaCl2 and 800 ppm of Ca(OH)2.
2nd Step precipitation is recommended for Scheme 3 for Fluoride removal.
XRF analysis would be done to ensure the purity of CaF2 is above 75% to meet requirement specified by Micron.

## Slide 20: Supplementary Jar Test results for HFW incoming

## Slide 21: Water Analysis of HFW Incoming
Elements | Concentration based on in-house measurement (ppm)
F | 555.8
Cl | 245.1
I | 6.26
NO3 | 82.1
NH3 | 6.1
Ca | 2.35
Fe | 0.171
Mg | 0.776
Ni | 0.586
K | 0.813
SiO2 | 19.8
Na | 504
Elements | Characteristics based on in-house measurements | Units
pH | 3.27 | -
Conductivity | 2132 | µS/cm
Colour (True) | 1,310 | Pt/Co
TDS | 1143 | mg/l
Turbidity | 154 | NTU
TSS | 70 | mg/l
TOC | 28 | mg/l
COD | 334 | O2 mg/l
Total Chlorine | 1.57 | mg/l

## Slide 22: Jar testing of HFW Incoming with Lime
Incoming HFW with added lime in
different dosages
(5000 ppm, 6000 ppm, 7000 ppm)
Solution after the addition of Flocculant (AN 905 SH) Precipitates clumped and settled after the addition of flocculant.

## Slide 23: Jar testing of HFW Incoming with Lime
Jar | Lime dosage (ppm) | Ph |  | 
 |  | t = 0 min | t = 15 min | t = 30 min
1 | 5000 | 3.3 | 12.6 | 12.5
2 | 6000 | 3.3 | 12.6 | 12.5
3 | 7000 | 3.3 | 12.6 | 12.5
Chemical precipitation with different ppm of Ca(OH)2
Coagulation and flocculation with 1 mg/L anionic polymer (Flopam AN 905 SH)
Jar | Lime dosage (ppm) | pH |  |  | Polymer used
 |  | t = 0 min | t = 15 min | t = 30 min | 
1 | 5000 | 12.5 | 12.5 | 12.5 | Flopam AN 905 SH
2 | 6000 | 12.5 | 12.5 | 12.5 | 
3 | 7000 | 12.5 | 12.5 | 12.5 | 

## Slide 24: Jar testing of HFW Incoming with Lime
Elements | Concentration based on in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3
Lime dosage | - | 5000 | 6000 | 7000
pH | 3.27 | 12.49 | 12.39 | 12.51
Conductivity | 2,132 µS/cm | 10680 µS/cm | 10220 µS/cm | 10330 µS/cm
Turbidity | 154 NTU | 23.7 NTU | 9.8 NTU | 10.4 NTU
F | 555.8 | 8.516 | 7.875 | 7.371
Cl | 245.1 | 88.446 | 36.321 | 36.69
SO4 | <0.1 | 41.562 | 13.358 | 9.666
NO3 | 82.1 | 76.863 | 78.483 | 77.662
NH3 | 6.1 | 4.8 | 5.3 | 3.4
Ca | 2.35 | 421 | 694 | 633
Fe | 0.171 | <0.1 | <0.1 | <0.1
Mg | 0.776 | <0.1 | <0.1 | <0.1
Ni | 0.581 | <0.1 | <0.1 | <0.1
K | 0.813 | 8.82 | 5.05 | 5.42
SiO2 | 19.8 | <0.1 | <0.1 | <0.1
Na | 504 | 614 | 639 | 581
Notes: Might want to remove sulfate row.

## Slide 25: Jar testing of HFW Incoming with Lime
Jar | Lime dosage (ppm) | Weight of Wet Sludge (g) | Weight of Dry Sludge (g) | Moisture Content of Wet Sludge
1 | 5000 | 11.985 | 4.037 | 66.3%
2 | 6000 | 13.304 | 4.851 | 63.5%
3 | 7000 | 14.051 | 5.745 | 59.1%
Sludge collected from vacuum filtration and dried in 80C oven.