## Slide 1
MICRON – HF WASTEWATER TREAMENT
SIMULATION & BENCH TESTING – Dec 2021
Siva Kumar Kota/Chun Yew
Hiep Le/Sankar

## Slide 2
HFW Treatment Objectives
The objectives of simulation and bench testing are
  To identify the optimized flow scheme to treat HFW wastewater
  To compare the treatability of the HFW wastewater between Calcium hydroxide and Calcium chloride.
  To compare the quantity and quality of generated sludge
  To meet sludge quality >80% of CaF2
  To meet discharge F<10ppm and TDS <3000 ppm

## Slide 3: Simulation summary
Option 1 – NF90/270 + BWRO
Option 1a – NF270 + BWRO (Two Pass)
Option 2 – NF270 + SWRO (Single Pass)
Option 3– NF270 + SWRO (1st pass) + BWRO (2nd pass)
Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)
Option 5– NF270 followed by SWRO (clarified water recycle)
Option 5a– NF270 followed by SWRO (separate sludge)
Option 6– NF270 followed by SWRO (F-800 ppm)
Option 6a– NF270 followed by SWRO (F-800 ppm and combined sludge)
Option 6b– NF270 followed by SWRO (F-600 ppm)
Option 7- HFW Effluent treatment
Notes: 600 ppm max
350 ppm avg

## Slide 4
Micron 10X – Influent Wastewater quality
Parameters | Unit | HF Wastewater
TDS | mg/L | 698
pH | - | 3.6
TSS | mg/L | 96.0
NH4 | mg/L | 207
HCO3 | As CaCO3 mg/L | <20
CO3 | As CaCO3 mg/L | <20
NO3 | mg/L | 73.4
SO4 | mg/L | 174
K | mg/L | 2.92
Na | mg/L | 250
Mg | mg/L | 0.085
Ca | mg/L | 0.20
Sr | mg/L | 0.00041
Ba | mg/L | 0.0016
Cl | mg/L | 25.1
Parameters | Unit | HF Wastewater
F | mg/L | 1136
SiO2 | mg/L | 50.8
B | mg/L | 0.25
Al | mg/L | 0.068
Br | mg/L | 30.3
Cu | mg/L | 0.0028
Fe | mg/L | 0.065
Mn | mg/L | 0.0058
TOC | mg/L | 75.8
O&G | mg/L | <10
PO4 | mg/L | 12.3
COD | mg/L | 280
Total Hardness | As CaCO3 mg/L | 0.85
Total Alkalinity | As CaCO3 mg/L | <20

## Slide 5
Option1 - NF90/270 + BWRO
5
BWRO
NF
HF WW
Polishing Filters
Coagulation, Clarifier
sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
F: 105 m3/hr
F:404 mg/l
PO4: 0 mg/l
F: 90 m3/hr
F:30 mg/l
PO4: 0 mg/l
F: 61 m3/hr
F:3957 mg/l
PO4: 355,2 mg/l
F: 85 m3/hr
F:<10 mg/l
PO4: 0 mg/l
reject
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 6
Simulation summary
6
Performed different simulations/projections for the scheme UF, NF & RO scheme
UF:
  WW contains high amount of TSS (96 mg/l) and TOC (>50 mg/l).
  Achieved recovery ~84% at 41 LMH
NF & RO:
  Tried different types of membranes (tighter vs loose membrane)
  WW contains high amount of F (1136 mg/l) and Phosphate (100 mg/l).
  Tighter membrane:
    Phosphate rejection>99.5%
    Fluoride rejection~70%
  Loose membrane:
    Phosphate rejection>99.5%
    Fluoride rejection : 30-40%
  Overall system recovery ~72%
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 7: UF Projections
NF
RO

## Slide 8: NF & RO Projections
NF
RO

## Slide 9: NF & RO Projections Contd.,
NF – Tighter membrane
BWRO

## Slide 10: NF & RO Projections Contd.,
NF – Loose membrane
BWRO

## Slide 11
Option1a - NF270 + BWRO (Two Pass)
11
BWRO (2 pass)
NF270
HF WW
Treated Water
Polishing Filters
Coagulation, Clarifier
sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
reject
UF
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
SWRO – 1 PASS
BWRO -2 PASS
SWRO + BWRO
Treated water BWRO

## Slide 12: Option 1a – NF270 + BWRO (TWO Pass)

## Slide 13: Option 1a – NF270 + BWRO (TWO Pass)
NF 270– Loose membrane

## Slide 14: Option 1a – NF270 + BWRO (TWO Pass)
1st Pass BWRO
2nd Pass BWRO

## Slide 15
Option 2 - NF270 + SWRO (SINGLE Pass)
15
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 16: Option 2 – NF270 + SWRO (SINGLE Pass)

## Slide 17: Option 2 – NF270 + SWRO (SINGLE Pass)
NF270
SWRO

## Slide 18: Option 3– NF270 + SWRO (1st pass) + BWRO (2nd pass)
BWRO (2nd pass)
Chemical Parameters |  | 
Ammonia (as N) | mg/L | <1.0
Aluminium | mg/L | <0.1
Barium | mg/L | <0.1
Boron | mg/L | <0.5
Calcium | mg/L | <20
Chloride | mg/L | <20
Copper | mg/L | <0.05
Fluoride | mg/L | <0.5
Iron | mg/L | <0.04
Manganese | mg/L | <0.05
Nitrate (as N) | mg/L | <5
Sodium | mg/L | <20
Sulphate | mg/L | <5
Silica (as SiO2) | mg/L | <3
Strontium | mg/L | <0.1
Total Trihalomethanes Ratio | - | <0.04
Total Organic Carbon (TOC) | mg/L | <0.5
Total Hardness (as CaCO3) | mg/L | <50
Zinc | mg/L | <0.1
NEWater

## Slide 19: Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)

## Slide 20: Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)
NF270
SWRO (1st stage) + BWRO (2nd stage)

## Slide 21
Option 5 -NF270 followed by SWRO (clarified water recycle)
21
SWRO
NF 270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 22: Option 5– NF270 followed by SWRO
NF270

## Slide 23: Option 5– SWRO (NF permeate and F rich clarified water)
SWRO

## Slide 24
Option 5a - NF270 followed by SWRO (separate sludge)
24
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM

## Slide 25: Option 5a – NF270 (Loose membrane)

## Slide 26: Option 5a – SWRO with pH adjustment

## Slide 27: NEWater spec
Chemical Parameters |  | 
Ammonia (as N) | mg/L | <1.0
Aluminium | mg/L | <0.1
Barium | mg/L | <0.1
Boron | mg/L | <0.5
Calcium | mg/L | <20
Chloride | mg/L | <20
Copper | mg/L | <0.05
Fluoride | mg/L | <0.5
Iron | mg/L | <0.04
Manganese | mg/L | <0.05
Nitrate (as N) | mg/L | <5
Sodium | mg/L | <20
Sulphate | mg/L | <5
Silica (as SiO2) | mg/L | <3
Strontium | mg/L | <0.1
Total Trihalomethanes Ratio | - | <0.04
Total Organic Carbon (TOC) | mg/L | <0.5
Total Hardness (as CaCO3) | mg/L | <50
Zinc | mg/L | <0.1

## Slide 28: Option 5a – polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 29: Option 5a - NF270 Reject chemical precipitation using Ca(OH)2

## Slide 30: Option 5a- NF270 Reject chemical precipitation using Ca(OH)2

## Slide 31: Option 5a-SWRO Reject chemical precipitation

## Slide 32: Option 5a -SWRO Reject chemical precipitation

## Slide 33
Option 6 - NF270 followed by SWRO (F-800 ppm)
33
NF270
UF
HF WW
SWRO
Coagulation,Clarifier
Sludge
F: 150 m3/hr
F:800 mg/l
PO4: 100 mg/l
CoagulationClarifier
Sludge
BWRO (optional)
Stream 1
Stream 2
Stream 3
Stream 4
Stream 5
Stream 6
Stream 7
Stream 9
Stream 8
Stream 10
Stream 11
Polishing filters
Stream 12
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM
AMMONIUM PEROXIDE WASTE- H2O2
PETERG7@

## Slide 34: HFW – Feed Water Characteristics

## Slide 35: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 36: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 37: Option 6 – NF270+SWRO with 800 PPM of F
NF270
SWRO
Stream 4
Stream 9

## Slide 38: Option 6 – Polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 39: Option 6 – Polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 40: Option 6-NF270 Reject chemical precipitation using Ca(OH)2
Stream 6-sludge
Stream 419.3 m3/hr
Stream 518 m3/hr

## Slide 41: Option 6- NF270 Reject chemical precipitation using Ca(OH)2
>80% of CaF2 sludge

## Slide 42: Option 6- SWRO Reject chemical precipitation
Stream 11-sludge
Stream 915.8 m3/hr
Stream 1014.8 m3/hr

## Slide 43: Option 6 -SWRO Reject chemical precipitation
>80% of CaF2 sludge

## Slide 44
Option 6a – NF270 followed by SWRO (F-800 ppm and combined sludge)
44
NF270
UF
HF WW
SWRO
Sludge
F: 150 m3/hr
F:800 mg/l
PO4: 100 mg/l
CoagulationClarifier
BWRO (optional)
Stream 1
Stream 2
Stream 3
Stream 4
Stream 6
Stream 9
Stream 5
Stream 10
Stream 7
Stream 8
Polishing filters
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM

## Slide 45: Option 6a–combined reject chemical precipitation –CaF2 sludge
Stream 7-sludge
Stream 4&535.3 m3/hr
Stream 633.5 m3/hr

## Slide 46: Option 6a–combined reject chemical precipitation –CaF2 sludge
>80% of CaF2 sludge

## Slide 47: Option 6b – NF270 + SWRO With 600 ppm of F

## Slide 48: Option 6b – NF270+SWRO WITH 600 PPM of F
NF270
SWRO

## Slide 49: Option 7-HFW Effluent treatment – UF, RO

## Slide 50: Option 7- HFW Effluent treatment ( UF & RO)

## Slide 51: Option 7- HFW Effluent treatment (UF& RO)
Pass 1 – BWRO
Pass 2 - BWRO

## Slide 52: Micron HFW Treatment -Next Steps and completion date
Sl.No. | Action Items | To be completed by | Remarks
1 | Perform projection to check the criticality of NF in this configuration If projection is good, will NF be a necessary unit operations here. What will be the benefits of incorporating NF in the design needs to be validated. | End/1st week of Dec | Will run few more simulations to validate the requirements
2 | The NaOH dosing for raising permeate Ph NaOH dosing requirement Final TDS | End/1st week of Dec | Will run few more simulations to validate the requirements
3 | Evaluate the effectiveness of Ca(OH)2 dosing by lab test Reaction rate with Ca(OH)2 Will increase of HRT help the completeness of reaction CaF2% in sludge to be validated for different water samples Settling velocity to be noted | End/1st week of Dec | Lab study
4 | As the projection data does not show on the TOC/IPA content in relevant streams, data to be generated based on some lab test or other projections | End/1st week of Dec | Lab study
5 | Na is coming into the streams due to ion balancing. Therefore, true presence of cations needs to be validated so that possible other contaminants issues can be identified. Clarified water characteristics RO permeate water characteristics | End/1st week of Dec | Simulations and lab study
6 | As neutralization with H2SO4 needs to take place for the clarified water, possibilities of any precipitation in the downstream to be verified | End/1st week of Dec | Simulations and lab study
7 | What will be the retrofits required if this system to be used for CMP waste-CMP WW Characteristics will be given later. | End/1st week of Dec | TBD
Notes: 200 micro siemens/cm
Solids – silica, abrasive,
No chemicals
ADD SLIDES for synthetic water

## Slide 53: Action item 1 – Feasibility of SWRO +BWRO With 800 ppm of F

## Slide 54: Action item 1 – Feasibility of SWRO +BWRO With 800 ppm of F

## Slide 55: Action item 1 – Feasibility of SWRO +BWRO With 800 ppm of F
SWRO
BWRO

## Slide 56: Action item 2: Permeate Ph adjustments
SWRO
pH adjustment

## Slide 57: Action item 2: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 58: Action item 2: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 59: Action item 2: Option 6 – NF270+SWRO WITH 800 PPM of F
NF270
SWRO

## Slide 60: Action item 2: Option 6 – polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 61: Action item 2: Option 6 – polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 62: Action item2: Option 6a–combined reject chemical precipitation

## Slide 63: Action item 2: Option 6a–combined chemical precipitation –CaF2 sludge
>80% of CaF2 sludge

## Slide 64: Action item 3: Preparation of Synthetic Combined NF RO Reject Solution (with pH adjustment)
Preferred chemicals | Required quantity for 1 Liter solution (gram)
NH4Cl | 0.210
NaCl | 0.064
CaCl2 | 0.049
HF | 2.986
H3PO4 | 0.367
SiH2O3 | 0.138
H2SO4 | 0.362
Elements | Desired concentration (ppm) | Calculated concentration based on added chemicals (ppm) | Concentration based on in-house measurement (ppm)
pH | 3.5 | - | 3.5
Conductivity | - | - | 6,375 µS/cm
TDS | - | - | 3,394
NH4 | 70.8 | 70.8 | 65.8
F | 2,835 | 2,835 | 2,928
SO4 | 355 | 355 | 345
PO4 | 356 | 356 | 366
Cl | 209 | 209 | 211
Na | 2,790 | 24.99 | 500
Ca | 17.7 | 17.7 | 11.1
Si | 49.5 | 49.5 | 47.6

## Slide 65: Jar testing Procedure
To each testing jar, pour in 1L of wastewater sample
To each jar, dose in 7000/7500/8000 mg/L of Ca(OH)2 and rapid mix for 30s
Slow mix for 30 min, measure pH every 10 min
Dose 1mg/L for each of the SNF polymer (anionic) in each jar and further slower mix (30 rpm) for 30 min. Measure pH every 20 min
Stop mixing and leave the solids to settle over 60 min
Observe sludge settling and measure sludge height every 5 min (if applicable)
Measure turbidity of supernatant and collect the sludge
For the jar with the lowest supernatant turbidity reading, filter out the supernatant through 0.45 um filter and send for analysis and collect the sludge generated
For the sludge collected, filter out using 1.5 µm filter. Collect the sludge, dry sample for XRD analysis. Meanwhile, dissolve a pre-determined amount of collected sludge in acid and send for analysis

## Slide 66: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 1
Synthetic combined reject solution in different jars
Synthetic combined reject solution with added lime at different dosages (7000, 7500, 8000 ppm)
Solution with added flocculant (Flopam AN 934 SH). Precipitates clumped and settled after the addition of flocculant.

## Slide 67: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 1
Jar | Lime dosage (ppm) | pH |  | 
 |  | t = 15 min | t = 20 min | t = 30 min
1 | 7000 | 4.82 | 6.49 | 8.97
2 | 7500 | 9.98 | 11.08 | 11.46
3 | 8000 | 11.69 | 11.81 | 11.93
Chemical precipitation with Ca(OH)2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | Lime dosage (ppm) | pH |  |  | Polymer used
 |  | t = 10 min | t = 20 min | t = 30 min | 
1 | 7000 | 9.03 | 9.23 | 9.22 | Flopam AN 934 SH
2 | 7500 | 11.45 | 11.47 | 11.43 | Flopam AN 934 SH
3 | 8000 | 12.01 | 12.05 | 12.00 | Flopam AN 934 SH

## Slide 68: Jar testing of Synthetic Combined NF RO Reject
Chart: Variations in the pH with respect to time and different lime dosages
| 0 | 15 | 20 | 30
pH @7000 | 3.5 | 4.82 | 6.49 | 8.49
pH @7500 | 3.5 | 9.98 | 11.08 | 11.46
pH @8000 | 3.5 | 11.69 | 11.81 | 11.93

## Slide 69: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 1
Elements | Concentration based on in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3
pH | 3.5 | 9.22 | 11.43 | 12
Conductivity | 6,375 µS/cm | 2,324 µS/cm | 2,338 µS/cm | 3,115 µS/cm
TDS | 3,394 | 1,177 | 1,185 | 1,603
NH4 | 65.8 | 67.4 | 55.7 | 51.6
F | 2,928 | 210 | 137 | 60.3
SO4 | 345 | 207 | 216 | 179
PO4 | 366 | <1 | <1 | <1
Cl | 211 | 192 | 194 | 194
Na | 500 | 493 | 459 | 478
Ca | 11.1 | 1.43 | 2.58 | 9.57
Si | 47.6 | 21.7 | 1.86 | 0.308
Jar | Polymer added | Lime dosage (ppm) | Supernatant turbidity (NTU)
1 | Flopam AN 934 SH | 7000 | 0.39
2 | Flopam AN 934 SH | 7500 | 0.33
3 | Flopam AN 934 SH | 8000 | 1.08

## Slide 70: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 2
Synthetic combined reject solution in different jars, with added different chemicals. Jar 1 from the left most to jar 4 in right most.
Starting of settling
End of settling

## Slide 71: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment )– Testing 2
Jar | Chemical dosage | pH |  | 
 |  | t = 10 min | t = 20 min | t = 30 min
1 | 10,000 ppm lime | 12.52 | 12.59 | 12.62
2 | 12,000 ppm lime | 12.65 | 12.70 | 12.71
3 | 5,000 ppm lime + 5,000 ppm CaCl2 | 2.04 | 2.08 | 2.13
4 | 6,000 ppm lime + 6,000 ppm CaCl2 | 2.38 | 2.94 | 4.81
Chemical precipitation with Ca(OH)2 (lime) and CaCl2
Coagulation and flocculation with 1 mg/L anionic polymer
Jar | Chemical dosage | pH |  |  | Polymer used
 |  | t = 2 min | t = 10 min | t = 30 min | 
1 | 10,000 ppm lime | 12.58 | 12.54 | 12.56 | Flopam AN 934 SH
2 | 12,000 ppm lime | 12.67 | 12.72 | 12.65 | Flopam AN 934 SH
3 | 5,000 ppm lime + 5,000 ppm CaCl2 | 2.13 | 2.13 | 2.09 | Flopam AN 934 SH
4 | 6,000 ppm lime + 6,000 ppm CaCl2 | 6.21 | 6.29 | 6.48 | Flopam AN 934 SH

## Slide 72: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 2
Elements | Concentration based on in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3 | Supernatant quality for Jar 4
pH | 3.5 | 12.56 | 12.65 | 2.09 | 6.48
Conductivity | 6,375 µS/cm | 8,233 µS/cm | 10.64 mS/cm | 11.76 mS/cm | 10.43 mS/cm
TDS | 3,394 | 4,460 | 5,867 | 6,526 | 5,745
NH4 | 65.8 | 57 | 59.4 | 68.4 | 72.6
F | 2,928 | 8.21 | 5.61 | 187 | 610
SO4 | 345 | 72.4 | 50.6 | 32 | 96.3
PO4 | 366 | <1 | <1 | 241 | 83
Cl | 211 | 191 | 164 | 2,939 | 3,548
Na | 500 | 353 | 343 | 365 | 402
Ca | 11.1 | 389 | 622 | 1,077 | 2,139
Si | 47.6 | <0.1 | <0.1 | 65.2 | 66.7
Jar | Polymer added | Chemicals dosage | Supernatant turbidity (NTU)
1 | Flopam AN 934 SH | 10,000 ppm lime | 20.8
2 | Flopam AN 934 SH | 12,000 ppm lime | 74.2
3 | Flopam AN 934 SH | 5,000 ppm lime + 5,000 ppm CaCl2 | 430
4 | Flopam AN 934 SH | 6,000 ppm lime + 6,000 ppm CaCl2 | 496

## Slide 73: Action item 3: Jar testing of Synthetic Combined NF RO Reject (with pH adjustment) – Testing 3
Elements | Concentration based on in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2 | Supernatant quality for Jar 3 | Supernatant quality for Jar 4 | Supernatant quality for Jar 5
pH | 3.5 | 11.96 | 11.91 | 12.03 | 11.91 | 9.8
Conductivity | 6,375 µS/cm | 8889 µS/cm | 17.23 mS/cm | 11.93 mS/cm | 14.4 mS/cm | 7756 µS/cm
TDS | 3,394 | 4844 | 9824 | 6624 | 8108 | 4180
F | 2,928 | 9.15 | 13 | 29.1 | 14 | 14.2
SO4 | 345 | 116 | 117 | 114 | 114 | 106
PO4 | 366 | <1 | <1 | 3.14 | <1 | <1
Cl | 211 | TBC | TBC | TBC | TBC | 2376
Na | 500 | 440 | 496 | 440 | 434 | 429
Ca | 11.1 | 1098 | 2858 | 1738 | 2263 | 920
Si | 47.6 | 0.149 | 0.342 | 0.863 | 0.356 | 10.5
Jar | Polymer added | Chemical's dosage | Supernatant turbidity (NTU)
1 | Flopam AN 934 SH | 8000 ppm lime + 4000 ppm CaCl2 | 56.9
2 | Flopam AN 934 SH | 8000 ppm lime + 10000 ppm CaCl2 | 226
3 | Flopam AN 934 SH | 8000 ppm lime + 6000 ppm CaCl2 | 138
4 | Flopam AN 934 SH | 8000 ppm lime + 8000 ppm CaCl2 | 162
5 | Flopam AN 934 SH | 6000 ppm lime + 4000 ppm CaCl2 | 22

## Slide 74: Action item 3 : XRD analysis of CaF2 sludge
Synthetic combined reject solution with added lime at 7500 PPM
Notes: Area

## Slide 75: Action item 4: Preparation of Synthetic HFW+NH4F Solution (with pH adjustment)
Preferred chemicals | Required quantity for 1 Liter solution (gram)
NH4Cl | 0.059
NaCl | 0.013
CaCl2 | 0.014
HF | 0.843
H3PO4 | 0.206
SiH2O3 | 0.039
H2SO4 | 0.102
Elements | Desired concentration (ppm) | Calculated concentration based on added chemicals (ppm) | Concentration based on in-house measurement (ppm)
pH | 3.5 | - | 3.5
Conductivity | - | - | 2,481 µS/cm
TDS | - | - | 1,263
NH4 | 20 | 20 | 19.2
F | 800 | 800 | 789
SO4 | 100 | 100 | 98
PO4 | 200 | 200 | 205
Cl | 50 | 55.86 | 62.9
Na | 5 | 5 | 339
Ca | 5 | 5 | 4.05
Si | 14.02 | 14.02 | 16.2

## Slide 76: Action item 4: Anti-scalant compatibility test - NF filtration of HFW+NH4F with IPA (with pH adjustment)
Anti-scalant | pH | Solution appearance
AS1 | 3.0 | Clear
AS2 | 7.19 | Clear
AS3 | 3.7 | Clear
AS4 | 3.58 | Clear
Initial solution pH: 3.3, pH adjusted to 3.5
AS4 was selected for the NF filtration experiment because its addition into the feed solution didn’t alter the solution pH much.

## Slide 77: Action item 4: Result of NF filtration of HFW+NH4F with IPA (with pH adjustment)
Elements | Concentration for synthetic feed (ppm) | Concentrated feed (ppm) | Permeate (ppm)
pH | 3.5 | 5.04 | 3.29
Conductivity | 3,357 µS/cm | 9,022 µS/cm | 708.6 µS/cm
TDS | 1,134 | 4,921 | 344.4
NH4 | 19.7 | 50.1 | 12.2
F | 819 | 1,555 | 144
SO4 | 100 | 389 | 3.83
PO4 | 214 | 637 | 1.55
Cl | 54.3 | 178 | 21
Na | 721 | 2082 | 86
Ca | 1.49 | <0.1 | <0.1
Si | 12.7 | 73.9 | 51.9
COD | 2,450 | 3935 | 1580
TOC | 473 | 870 | 382
IPA | TBC | TBC | TBC

## Slide 78: Action item 5: Preparation of Synthetic Combined NF RO Reject Solution (without pH adjustment)
Preferred chemicals | Required quantity for 1 Liter solution (gram)
NH4Cl | 0.209
NaCl | 0.011
CaCl2 | 0.049
HF | 2.242
H3PO4 | 0.367
SiH2O3 | 0.128
H2SO4 | 0.362
Elements | Desired concentration (ppm) | Calculated concentration based on added chemicals (ppm) | Concentration based on in-house measurement (ppm)
pH | 1.9 | - | 3
Conductivity | - | - | 7745 µS/cm
TDS | - | - | 4175
NH4 | 70.6 | 70.6 | TBC
F | 2129 | 2129 | 2304
SO4 | 355 | 355 | TBC
PO4 | 356 | 356 | 389
Cl | 177 | 177 | TBC
Na | 17.6 | 4.49 | 7.74
Ca | 17.7 | 17.7 | 7.94
Si | 46.2 | 46.2 | 41.2

## Slide 79: Action item 5: Jar testing of Synthetic Combined NF RO Reject (without pH adjustment)– Testing 4
Elements | Concentration based on in-house measurement (ppm) | Supernatant quality for Jar 1 | Supernatant quality for Jar 2
pH | 3 | 9.68 | 9.29
Conductivity | 7745 | 1941 µS/cm | 7256 µS/cm
TDS | 4175 | 974.7 | 3889
F | 2304 | 22 | 7.51
SO4 | TBC | 150 | 137
PO4 | 389 | <1 | <1
Na | 7.74 | 8.2 | 25.4
Ca | 7.94 | 295 | 1290
Si | 41.2 | 14.9 | 5.66
Jar | Polymer added | Chemical's dosage | Supernatant turbidity (NTU)
1 | Flopam AN 934 SH | 6000 ppm lime + 500 ppm CaCl2 | 9.98
2 | Flopam AN 934 SH | 6000 lime + 4000 ppm CaCl2 | 20.4

## Slide 80: Action item 5: Preparation of Synthetic HFW+NH4F with IPA (without pH adjustment)
Preferred chemicals | Required quantity for 1 Liter solution (gram)
NH4Cl | 0.059
NaCl | 0.013
CaCl2 | 0.014
HF | 0.843
H3PO4 | 0.206
SiH2O3 | 0.039
H2SO4 | 0.102
IPA | 1
Elements | Desired concentration (ppm) | Calculated concentration based on added chemicals (ppm) | Concentration based on in-house measurement (ppm)
pH | - | - | 2.92
Conductivity | - | - | 3371 µS/cm
TDS | - | - | 1741
NH4 | 20 | 20 | TBC
F | 800 | 800 | 802
SO4 | 100 | 100 | TBC
PO4 | 200 | 200 | 161
Cl | 50 | 55.86 | TBC
Na | 5 | 5 | 10.1
Ca | 5 | 5 | 4.6
Si | 14.02 | 14.02 | 9.15
COD | - | - | 2523
TOC | - | - | 588
IPA | 1,000 | 1,000 | TBC

## Slide 81: Action item 5: Results of NF filtration of HFW+NH4F with IPA (without pH adjustment)
Elements | Concentration for synthetic feed (ppm) | NF concentrated feed (ppm) | NF Permeate (ppm)
pH | 2.92 | 2.08 | 2.26
Conductivity | 3371 µS/cm | 4821 µS/cm | 3071 µS/cm
TDS | 1741 | 2535 | 1580
F | 802 | 1328 | 456
SO4 | TBC | 201 | 88.9
PO4 | 161 | 203 | 150
Cl | TBC | 152 | 147
Na | 10.1 | 30.9 | 4.72
Ca | 4.6 | 21.5 | 0.105
Si | 9.15 | 41.5 | 4.19
COD | 2523 | 2970 | 2013
TOC | 588 | 691 | 484

## Slide 82: Action item6: supernatant pH adjustment using H2SO4

## Slide 83: Additional Action item: Feasibility of NF270 + SWRO With 800 ppm of F, 500 ppm of PO4 and 300 ppm of Sulphates

## Slide 84: Additional Action item: Feasibility of NF270 + SWRO With 800 ppm of F, 500 ppm of PO4 and 300 ppm of Sulphates

## Slide 85: Additional Action item: Feasibility of NF270 + SWRO With 800 ppm of F, 500 ppm of PO4 and 300 ppm of Sulphates
NF 270
SWRO

## Slide 86: Additional Action item: Combined reject chemical precipitation

## Slide 87: Conclusions
Following conclusions are made based on several RO/NF projections, bench scale testing and PHREEQC models
UF, NF and SWRO will be sufficient for generating required water quality for cooling tower and local scrubbers. Recovery ratio between 55-60%.
Lower pH will be helpful to get higher membrane rejections. No scaling issues with lower pH. Conventional membranes will be used for pH between 2 to 12
Mixed/NF +SWRO reject for removal of Fluoride (by coagulation, flocculation, clarification, sedimentation, filter press) looks a suitable configuration.
Lime and CaCl2 combination or higher amount of lime will be enough for the removal of fluoride to meet the discharge water quality.
Sludge will contain more than 80% of CaF2. if in case phosphates are higher, then sludge quality will differ. XRD results shows the major peak is CaF2.
NF will be having tolerance to the organics. Experiments are on going to validate the % IPA rejections.
Optimization of chemical dosage/conditions can be done during detailed engineering design

## Slide 88: Back up