## Slide 1: Micron IPAL
Application Team
Sep 2024
Rev 2

## Slide 2: Overall Objectives
To conduct ROi trial with Micron IPAL Synthetic Feed to achieve:
1. ROi system recovery of 92%
2. Final Reject IPA Concentration = 24,992 mg/L
3. Final Permeate IPA Concentration = 0.7 mg/L

## Slide 3: Projection
Overall recovery rate = 92.0% |  |  |  |  |  |  |  |  |  |  |  |  | 
Parameter | UNIT | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
List of Substance |  | RO P1 Inlet | RO P1 Reject | RO P1 Permeate | RO P2 Inlet | RO P2 Reject | RO P2 Permeate | RO P3 Inlet | RO P3 Reject | RO P3 Permeate | RO P4 Inlet | RO P4 Reject | RO P4 Permeate
Pass Recovery |  |  |  | 93.0% |  |  | 90.2% |  |  | 80.2% |  |  | 70.0%
Average Flowrate | m3/h | 24.3 | 1.6 | 21.1 | 27.6 | 2.7 | 24.9 | 32.8 | 6.5 | 26.3 | 26.3 | 7.9 | 18.4
Average Flowrate | gpm | 107 | 7 | 93 | 121 | 12 | 110 | 144 | 29 | 115 | 115 | 35 | 81
Pressure | barg | 24.4 | 3.0 | 1.0 | 23.5 | 3.0 | 1.0 | 20.0 | 3.0 | 1.0 | 19.5 | 3.0 | 1.0
Pressure | psig | 354.0 | 43.5 | 14.5 | 340.5 | 43.5 | 14.5 | 290.5 | 43.5 | 14.5 | 283.5 | 43.5 | 14.5
pH |  | 10 | 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 9 - 10 | 8 - 9
Operating Temperature | oC | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Operating Temperature | oF | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
Total Suspended Solids (TSS) | mg/l | <5 | <62.5 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
Total Dissolved Solids (TDS) | mg/l | 165 | 1250 | 0.3 | 0.2 | 2.3 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0
Chemical Oxygen Demand (COD) | mg/l | 9478 | 59981 | 1819 | 1656 | 14205 | 295 | 242 | 1126 | 24 | 24 | 76 | <1
Total Organic Carbon (TOC) | mg/l | 3554 | 22493 | 682 | 621 | 5327 | 111 | 91 | 422 | 9 | 9 | 28 | 0.6
Isopropyl alcohol (IPA) | mg/l | 3949 | 24992 | 758 | 690 | 5919 | 123 | 101 | 469 | 10 | 10 | 32 | 0.7
Isopropyl alcohol (IPA) | % | 0.39% | 2.50% | 0.08% | 0.07% | 0.59% | 0.01% | 0.01% | 0.05% | 0.0010% | 0.0010% | 0.003% | 0.0001%
Type of Flow |  | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous | Continuous

## Slide 4: Process Flow Diagram

## Slide 5: Lab skid

## Slide 6: Test Methodology
Prepare Synthetic Feed – 102L
  Synthetic feed was prepared with tap water and 99.5% IPA solution.
  pH adjustment from pH 7.53 to 10.21 was performed by dosing 50% NaOH (3.012 mL)
Perform water analysis
  Analyse synthetic feed with RI, ICP-OES, IC, TOC & COD analysers.
Perform pretreatment testing
  Prepare IPA calibration curves for RI, TOC and COD.
  Perform antiscalant projections to determine necessity of pretreatment, antiscalant type, and dosage.
Perform ROI concentration testing
  Load Pro-LF1 membranes into pressure vessels
  Start the pumps to circulate the feed water into the system with reject returned into feed tank while permeate is collected separately
  Record flow rates, pressures & collect samples for RI, COD, TOC analysis (conversion to [IPA] by calibration curve) at regular intervals
  Stop current ROI stage testing when expected volume of permeate is generated
  Collect samples of feed, permeate & reject for water analysis
  Further concentration of feed is required if target IPA concentration for reject is not achieved.

## Slide 7: Determining IPA Concentrations using RI, TOC and COD
IPA standards ranging from 0 to 30,000 mg/L were prepared and sent for RI, TOC and COD analysis.
Graphs of RI, TOC and COD values obtained against IPA concentrations were plotted.

## Slide 8: RI Calibration Graphs
Concentration of IPA (mg/L) | RI meter reading
0 | 1.3326
25 | 1.3325
50 | 1.3325
100 | 1.3325
251 | 1.3326
502 | 1.3326
1005 | 1.3326
2512 | 1.3327
5024 | 1.3330
10048 | 1.3335
25120 | 1.3349
30144 | 1.3351
Chart: Refractive Index (RI) against IPA Concentration (mg/L)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 1.3326 | 1.3325 | 1.3325 | 1.3325 | 1.3326 | 1.3326 | 1.3326 | 1.3327 | 1.333 | 1.3335 | 1.3349 | 1.3351
Chart: Refractive Index (RI) against IPA Concentration (mg/L)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 1.3326 | 1.3325 | 1.3325 | 1.3325 | 1.3326 | 1.3326 | 1.3326 | 1.3327 | 1.333 | 1.3335 | 1.3349 | 1.3351
RI is not capable of measuring [IPA] < 5000 mg/L.

## Slide 9: RI, TOC and COD Readings for Samples with different [IPA]
TOC (mg/L) | [IPA] from TOC (mg/L)
2383 | 4107
3518 | 6121
3903 | 6804
4739 | 8287
5881 | 10313
7836 | 13782
9717 | 17120
14200 | 25074
24950 | 44148
Refractive index is not used in this study for obtaining [IPA].
Refractive Index | [IPA] from RI (mg/L) | RI Deviation from TOC (%)
- | - | -
1.3328 | 3333 | -46%
1.3329 | 4444 | -35%
1.3330 | 5556 | -33%
1.3332 | 7778 | -25%
1.3336 | 12222 | -11%
1.3338 | 14444 | -16%
1.3344 | 21111 | -16%
1.3364 | 43333 | -2%
COD (mg/L) | [IPA] from COD (mg/L) | COD Deviation from TOC (%)
9900 | 4044 | -2%
14500 | 6019 | -2%
16730 | 6976 | 3%
19800 | 8294 | 0%
27000 | 11384 | 10%
33700 | 14260 | 3%
39000 | 16535 | -3%
57400 | 24433 | -3%
105600 | 45123 | 2%

## Slide 10: COD Calibration Graphs
Concentration of IPA (mg/L) | Expected COD reading (mg/L) | Actual COD reading (mg/L) | COD Deviation
0 | 0.0 | 0 | -
25 | 60.2 | 75 | 25%
50 | 120.4 | 146 | 21%
100 | 240.8 | 269 | 12%
251 | 601.9 | 635 | 6%
502 | 1203.8 | 1246 | 4%
1005 | 2407.5 | 2515 | 4%
2512 | 6018.8 | 6320 | 5%
5024 | 12037.5 | 13520 | 12%
10048 | 24075.1 | 26450 | 10%
25120 | 60187.7 | 56900 | 5%
30144 | 72225.2 | 71400 | 1%
Average COD Deviation |  |  | 10%
Chart: COD (mg/L) against IPA Concentration (mg/L)
| 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 75 | 146 | 269 | 635 | 1246 | 2515 | 6320 | 13520 | 26450 | 56900 | 71400
Chart: COD (mg/L) against IPA Concentration (mg/L)
| 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 75 | 146 | 269 | 635 | 1246 | 2515 | 6320 | 13520 | 26450 | 56900 | 71400
Chart: COD (mg/L) against IPA Concentration (mg/L) (Low Range)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005
 | 0 | 75 | 146 | 269 | 635 | 1246 | 2515 | 6320

## Slide 11: TOC Calibration Graphs
Concentration of IPA (mg/L) | Expected TOC reading (mg/L) | Actual TOC Reading (mg/L) | TOC Deviation
0 | 0 | 1.465 | -
25 | 15 | 14.7 | -2%
50 | 30 | 34.8 | 16%
100 | 60 | 57.3 | -5%
251 | 150 | 141 | -6%
502 | 301 | 299 | -1%
1005 | 602 | 574 | -5%
2512 | 1505 | 1396 | -7%
5024 | 3009 | 3612 | 20%
10048 | 6019 | 5690 | -5%
25120 | 15047 | 13980 | -7%
30144 | 18056 | 17170 | -5%
Average TOC Deviation |  |  | -1%
Chart: TOC (mg/L) against IPA Concentration (mg/L)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 1.465 | 14.7 | 34.76 | 57.3 | 141.3 | 298.55 | 573.5 | 1396 | 3612 | 5690 | 13980 | 17170
Chart: TOC (mg/L) against IPA Concentration (mg/L)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2 | 502.4 | 1004.8 | 2512.0000000000005 | 5024.0000000000009 | 10048.000000000002 | 25120.000000000004 | 30144
 | 1.465 | 14.7 | 34.76 | 57.3 | 141.3 | 298.55 | 573.5 | 1396 | 3612 | 5690 | 13980 | 17170
Chart: TOC (mg/L) against IPA Concentration (mg/L) (0-250 mg/L Range)
| 0 | 25.120000000000005 | 50.240000000000009 | 100.48000000000002 | 251.2
 | 1.465 | 14.7 | 34.76 | 57.3 | 141.3
Chart: TOC (mg/L) against IPA Concentration (mg/L) (0-50 mg/L range)
| 0 | 25.120000000000005 | 50.240000000000009
 | 1.465 | 14.7 | 34.76
Average deviation from expected reading is -1%, TOC calibration graph is used in this study to obtain [IPA].

## Slide 12: Water Analysis – Micron IPAL Feed
PARAMETER | METHOD | UNIT | IPAL P1 Inlet
pH | pH probe | - | 10.19
Conductivity | Conductivity probe | µS/cm | 285
Carbonate Alkalinity, CO3/ P-Alkalinity​ | APHA 2320B​ | CaCO3 mg/l​ | 25​
Bicarbonate Alkalinity, HCO3/ M-Alkalinity​ | APHA 2320B​ | CaCO3 mg/l​ | ​28
Total Alkalinity​ | APHA 2320B​ | CaCO3 mg/l​ | 53
Fluoride as F | Ion Chromatography | mg/l | 0.512
Chloride as Cl | Ion Chromatography | mg/l | 28.996
Phosphate as PO4 | Ion Chromatography | mg/l | <0.1
Sulphate as SO4 | Ion Chromatography | mg/l | 38.917
Nitrite as NO2 | Ion Chromatography | mg/l | <0.1
Nitrate as NO3 | Ion Chromatography | mg/l | 2.773
Aluminium as Al | EPA200.7 | mg/l | <0.1
Boron as B | EPA200.7 | mg/l | 0.172
Calcium as Ca | EPA200.7 | mg/l | 11
Germanium as Ge | EPA200.7 | mg/l | 0.24
Magnesium as Mg | EPA200.7 | mg/l | 3.13
Potassium as K | EPA200.7 | mg/l | 15.6
Dissolved Silica SiO4 | EPA200.7/ Calculation | mg/l | 2.06
Sodium as Na | EPA200.7 | mg/l | 27.4
Total Hardness as CaCO3 | EPA200.7/ Calculation | mg/l | 40.3
TOC | APHA 5310B | mg/l | 2383
COD | Hach 8000 | O2 mg/l | 9900
TDS | Ultrameter | mg/l | 160
TDS | APHA 2540C | mg/l | 199

## Slide 13: Antiscalant Projection
Target recovery: 93%
pH adjusted from 7.5 to 10.21, using 50% NaOH (3.012 mL for 102L)
Antiscalant: Cure AT9530 @ 2 ppm
In this ROi trial, no antiscalant was dosed.

## Slide 14: Experiment 1.1: ROi Pass 1 Trial

## Slide 15: Objectives for Pass 1
To conduct ROi trial with Micron IPAL Synthetic Feed to achieve:
1. ROi system recovery of 93%
2. Pass 1 Reject IPA Concentration = 24,992 mg/L
3. Pass 1 Permeate IPA Concentration = 758 mg/L

## Slide 16: Water Analysis – Pass 1 Results
Time (minutes) | P1 Feed TDS (mg/L) | P1 Feed [IPA] from TOC (mg/L) | P1 Permeate TDS (mg/L) | P1 Permeate [IPA] from TOC (mg/L) | Volume of P1 Permeate Collected (L) | Recovery by Volume | Recovery by CF | Rejection by TOC
0 | 160.10 | 4107 | - | - | 0 | - | - | -
32 | 214.30 | 6121 | 15.30 | 91 | 33 | 0.32 | 0.33 | 0.985203
42 | 216.00 | 6804 | 3.37 | 111 | 45 | 0.44 | 0.40 | 0.983734
51 | 267.00 | 8287 | 3.32 | 139 | 55 | 0.54 | 0.50 | 0.983170
61 | 344.90 | 10313 | 2.65 | 167 | 65 | 0.64 | 0.60 | 0.983817
72 | 450.80 | 13782 | 2.18 | 231 | 75 | 0.74 | 0.70 | 0.983244
79 | 537.50 | 17120 | 2.34 | 303 | 80 | 0.78 | 0.76 | 0.982275
88 | 723.40 | 25074 | 3.45 | 486 | 87 | 0.85 | 0.84 | 0.980623
104 | 1283.00 | 44148 | 40.00 | 1318 | 95 | 0.93 | 0.91 | 0.970135
*Initial Feed Volume: 102L

## Slide 17: Water Analysis – Pass 1 Results: pH
Time (minutes) | P1 Feed [IPA] (mg/L) | P1 Feed pH | P1 Permeate [IPA] (mg/L) | P1 Permeate pH
0 | 4107 | 10.21 | - | -
32 | 6121 | 10.11 | 91 | 8.44
42 | 6804 | 10.05 | 111 | 8.78
51 | 8287 | 10.00 | 139 | 8.12
61 | 10313 | 10.01 | 167 | 8.86
72 | 13782 | 9.98 | 231 | 8.55
79 | 17120 | 9.97 | 303 | 8.76
88 | 25074 | 9.85 | 486 | 8.93
104 | 44148 | 9.59 | 1318 | 8.94
Notes: Mention P1 permeate IPA concentration might be even lower due to over-concentration (To add in discussion)

## Slide 18: ROi Concentration Results
Operating parameters:
- Average Feed pressure: 335 psi
- Average Feed Flow rate: 9 LPM
-Membrane: Pro-LF1
List of Substance | P1 Inlet | Final P1 Reject | Final P1 Permeate
Projection [IPA] (mg/L) | 3949 | 24992 | 758
Actual [IPA] (mg/L) | 4107 | 46383 | 210

## Slide 19: Flux Vs IPA Concentration
Chart: Pass 1 Flux (LMH) against Feed [IPA] (mg/L)
| 4106.7938254080909 | 6120.6334279630946 | 6803.7420156139106 | 8287.0635202271114 | 10313.323278921222 | 13782.095457771469 | 17119.56884315117 | 25073.791696238466 | 44147.602909865156
Flux against [IPA] | 28.1739 | 27.3913 | 26.8696 | 26.087 | 23.4783 | 20.3478 | 20.087 | 16.4348 | 11.4783

## Slide 20: Rejection Vs IPA Concentration
Chart: Pass 1 Rejection against Feed [IPA] (mg/L)
| 6120.6334279630946 | 6803.7420156139106 | 8287.0635202271114 | 10313.323278921222 | 13782.095457771469 | 17119.56884315117 | 25073.791696238466 | 44147.602909865156
Rejection against Feed [IPA] | 0.9852 | 0.98373 | 0.98317 | 0.98382 | 0.98324 | 0.98228 | 0.98062 | 0.97013

## Slide 21: Discussions
Time (Day) | P1 Permeate [IPA] from TOC (mg/L)
0 | 210
1 | 197
After 1 day, the IPA concentration of Pass 1 permeate decreased to 197 mg/L.
List of Substance | P1 Inlet | P1 Reject | P1 Permeate | P2 Inlet | P2 Reject | P2 Permeate | P3 Inlet | P3 Reject | P3 Permeate | P4 Inlet | P4 Reject | P4 Permeate
Projection [IPA] (mg/L) | 3949 | 24992 | 758 | 690 | 5919 | 123 | 101 | 469 | 10 | 10 | 32 | 0.7
Actual [IPA] (mg/L) | 4107 | 46383 | 210 | 197 | - | - | - | - | - | - | - | -
P1 Permeate value (197 mg/L) is closer to P3 Inlet (101 mg/L) than P2 Inlet (690 mg/L).
One pass is sufficient to achieve permeate with quality projected to be achieved with 2 passes.
Decreasing Pass 1 recovery may achieve P1 Reject and Permeate with closer values to projection.
Pass 2 is run with P2 Inlet = 197 mg/L instead.

## Slide 22: Conclusion
ROi recovery 91.1% (by CF) and 93% ( by Volume).
List of Substance | P1 Inlet | Final P1 Reject | Final P1 Permeate
Projection [IPA] (mg/L) | 3949 | 24992 | 758
Actual [IPA] (mg/L) | 4107 | 46383 | 210

## Slide 23: Experiment 1.2: ROi Pass 2 Trial

## Slide 24: Objectives for Projected Pass 2
To conduct ROi trial with Micron IPAL Synthetic Feed to achieve:
1. ROi system recovery of 90.2%
2. Pass 2 Reject IPA Concentration = 5919 mg/L
3. Pass 2 Permeate IPA Concentration = 123 mg/L

## Slide 25: Water Analysis – Pass 2 Results
Time (minutes) | P2 Feed TDS (mg/L) | P2 Feed [IPA] from TOC (mg/L) | P2 Permeate TDS (mg/L) | P2 Permeate [IPA] from TOC (mg/L) | Volume of P2 Permeate Collected (L) | Recovery by Volume | Recovery by CF | Rejection by TOC
0 | 20.43 | 197 | - | - | 0 | - | - | -
37 | 66.61 | 546 | 1.05 | 8.65 | 42 | 0.44 | 0.64 | 0.984162173
55 | 99.32 | 835 | 0.72 | 12.89 | 62 | 0.65 | 0.76 | 0.984552384
66 | 134.60 | 1132 | 1.14 | 15.01 | 73 | 0.77 | 0.83 | 0.986739039
72 | 175.80 | 1546 | 1.44 | 23.55 | 80 | 0.84 | 0.87 | 0.984767077
76 | 214.30 | 1991 | 1.04 | 29.46 | 84 | 0.88 | 0.90 | 0.985205993
*Initial Feed Volume: 95L

## Slide 26: Water Analysis – Pass 2 Results: pH
Time (minutes) | P2 Feed [IPA] (mg/L) | P2 Feed pH | P2 Permeate [IPA] (mg/L) | P2 Permeate pH
0 | 197 | 9.10 | - | -
37 | 546 | 9.64 | 8.65 | 8.2
55 | 835 | 9.68 | 12.89 | 8.59
66 | 1132 | 9.70 | 15.01 | 8.07
72 | 1546 | 9.58 | 23.55 | 8.57
76 | 1991 | 9.49 | 29.46 | 8.45

## Slide 27: ROi Concentration Results
Operating parameters:
- Average Feed pressure: 260 psi
- Average Feed Flow rate: 9 LPM
-Membrane: Pro-LF1
List of Substance | P2 Inlet | Final P2 Reject | Final P2 Permeate
Projection[IPA] (mg/L) | 690 | 5919 | 123
Actual [IPA] (mg/L) | 197 | 2356 | 12

## Slide 28: Flux Vs IPA Concentration
Chart: 
| 196.94648345687941 | 546.25040679804738 | 834.62502259989151 | 1132.0395950099437 | 1545.7080094015548 | 1991.1970710540591
Pass 2 Flux (LMH) against Feed [IPA] (mg/L) | 30 | 27.6522 | 28.6957 | 25.5652 | 26.8696 | 25.5652

## Slide 29: Rejection Vs IPA Concentration
Chart: 
| 546.25040679804738 | 834.62502259989151 | 1132.0395950099437 | 1545.7080094015548 | 1991.1970710540591
Rejection against Feed [IPA] (mg/L) | 0.98416 | 0.98455 | 0.98674 | 0.98477 | 0.98521

## Slide 30: Discussions
List of Substance | P1 Inlet | P1 Reject | P1 Permeate | P2 Inlet | P2 Reject | P2 Permeate | P3 Inlet | P3 Reject | P3 Permeate | P4 Inlet | P4 Reject | P4 Permeate
Projection [IPA] (mg/L) | 3949 | 24992 | 758 | 690 | 5919 | 123 | 101 | 469 | 10 | 10 | 32 | 0.7
Actual [IPA] (mg/L) | 4107 | 46383 | 210 | 197 | 2356 | 12 | 11 | - | - | - | - | -
Actual P2 Permeate value (12 mg/L) is close to P3 Permeate and P4 Inlet projection (10 mg/L).
Two passes were sufficient to achieve permeate with quality projected to be achieved with three passes.
Decreasing Pass 2 recovery may achieve P2 Reject and Permeate with closer [IPA] to projected values.
Pass 3 is run with P3 Inlet = 11 mg/L.
Time (Day) | P1 Permeate [IPA] from TOC (mg/L)
0 | 12
2 | 11
After 2 days, the IPA concentration of Pass 2 permeate decreased to 11 mg/L.
Notes: We do not have the concrete projection value, should we continue to concentrate down, we should be able to get close to P4 projected values.

## Slide 31: Conclusion
ROi recovery 91.6% (by CF) / 88.4% (by Volume).
List of Substance | P2 Inlet | P2 Reject Final | P2 Permeate Final
Projection[IPA] (mg/L) | 690 | 5919 | 123
Actual [IPA] (mg/L) | 197 | 2356 | 12

## Slide 32: Experiment 1.3: ROi Pass 3 Trial

## Slide 33: Objectives for Projected Pass 4
To conduct ROi trial with Micron IPAL Synthetic Feed to achieve:
1. ROi system recovery of 70.0%
2. Pass 4 Reject IPA Concentration = 32 mg/L
3. Pass 4 Permeate IPA Concentration = 0.7 mg/L

## Slide 34: Water Analysis – Pass 3 Results
Time (minutes) | P3 Feed TDS (mg/L) | P3 Feed [IPA] from TOC (mg/L) | P3 Permeate TDS (mg/L) | P3 Permeate [IPA] from TOC (mg/L) | Volume of P3 Permeate Collected (L) | Recovery by Volume | Recovery by CF | Rejection by TOC
0 | 33.00 | 11.32 | - | - | 0 | - | - | -
23 | 44.61 | 42.29 | 0.63 | 0.91 | 25 | 0.32 | 0.73 | 0.978373331
37 | 61.59 | 59.00 | 0.57 | 1.14 | 40 | 0.51 | 0.81 | 0.980759922
48 | 107.90 | 109.00 | 0.85 | 1.97 | 57 | 0.68 | 0.90 | 0.981999482
Initial Feed Volume: 84L
Notes: Check the TOC again and try to change the CF value, if possible.

## Slide 35: Water Analysis – Pass 3 Results: pH
Time (minutes) | P3 Feed [IPA] (mg/L) | P3 Feed pH | P3 Permeate [IPA] (mg/L) | P3 Permeate pH
0 | 11.32 | 8.73 | - | -
23 | 42.29 | 8.93 | 0.91 | 6.84
37 | 59 | 8.83 | 1.14 | 7.45
48 | 109 | 8.60 | 1.97 | 6.66

## Slide 36: ROi Concentration Results
Operating parameters:
- Average Feed pressure: 263 psi
- Average Feed Flow rate: 9 LPM
-Membrane: Pro-LF1
List of Substance | P4 Inlet | Final P4 Reject | Final P4 Permeate
Projection[IPA] (mg/L) | 10 | 32 | 0.7
Actual [IPA] (mg/L) | 11 | 135 | 0.44-2.40
List of Substance | TOC (mg/L) | [IPA] (mg/L)
P3 Permeate | 1.91 | 2.39
Tap Water | 1.29 | 1.45
P3 Permeate with [IPA] only | 0.62 | 0.44

## Slide 37: Flux Vs IPA Concentration
Chart: Pass 3 Flux (LMH) against Feed [IPA] (mg/L)
| 11.32 | 42.29 | 59 | 109
Pass 3 Flux (LMH) against [IPA] (mg/L) | 30 | 30 | 30.5217 | 28.9565

## Slide 38: Rejection Vs IPA Concentration
Chart: Rejection against Feed [IPA] (mg/L)
| 42.29 | 59 | 109
Rejection against [IPA] (mg/L) | 0.97848 | 0.98068 | 0.98193

## Slide 39: Discussions & Conclusions
List of Substance | P1 Inlet | P1 Reject | P1 Permeate | P2 Inlet | P2 Reject | P2 Permeate | P3 Inlet | P3 Reject | P3 Permeate | P4 Inlet | P4 Reject | P4 Permeate
Projection [IPA] (mg/L) | 3949 | 24992 | 758 | 690 | 5919 | 123 | 101 | 469 | 10 | 10 | 32 | 0.7
Actual [IPA] (mg/L) | 4107 | 46383 | 197 | 197 | 2356 | 12 | - | - | - | 11 | 135 | 0.44-2.40
Projection Recovery (% v/v) |  |  | 93.0 |  |  | 90.2 |  |  | 80.2 |  |  | 70.0
Actual Recovery (% v/v) |  |  | 93.1 |  |  | 88.4 |  |  | - |  |  | 67.9
Three passes were sufficient to achieve permeate with quality projected to be achieved with four passes.
Decreasing Pass 2 recovery may achieve P3 Reject and Permeate with [IPA] closer to Pass 4 projected values.
ROi recovery 91.6% (by CF) / 67.9% (by volume).