## Slide 1: Pilot Study Update
Client: Exyte
Location: Singapore
Date : 21 Feb 2024

## Slide 2: Note
Run 1 (Short term test) is completed on 2 Feb 2024.
Run 2 (Continuous test) is ongoing this week, aiming to complete on 23 Feb (Fri)

## Slide 3: Water analysis – Run 1
Sample | LSR A2 | HFW A1+A2 | HFW Gas Room | HFW Chem Room
pH | 3.93 | 3.48 | 3.15 | 2.71
Fluoride (mg/L) | 64 | 402 | 202 | 4358
Chloride (mg/L) | 11.1 | 481.7 | 10.7 | 18.5
Phosphate (mg/L) | <0.1 | 7.87 | 4.8 | 421.4
Sulfate (mg/L) | 4.0 | 6.3 | 2.4 | 5.9
Nitrate (mg/L) | 2.0 | 243.6 | 443.5 | 401.5
Ammonium as NH4 | 21.9 | 10.5 | 1.41 | 5.01
Calcium | 0.98 | 0.88 | 0.23 | 0.46
Magnesium | <0.1 | 0.315 | <0.1 | <0.1
Potassium | <0.1 | 0.238 | <0.1 | <0.1
Total Silica | 19.4 | 14.7 | 6.74 | <0.1
Sodium | 11.6 | 176 | 105 | 40.6
TOC | 7.35 | 25.7 | 9.64 | 31.7
Conductivity (uS/cm) | 354 | 1738 | 2010 | 7500
3

## Slide 4: Run 1 (Short term test) Experimental Procedure
Mixing ratio LSR A2: HFW A1+A2: Chem Room = 1:1:0.03 (600 L: 600L: 16L) found out from bench test
Fluoride = 307 mg/L in the mixture
To achieve the required amount of feed fluoride (F = 350 mg/L), 114 g NaF was added to make the feed solution for Run 1
2 ppm Vitec 4000 was added into the feed tank
SBRO experiment started with 15 mins service duration + 110 sec flushing duration
4

## Slide 5: Experimental conditions
Feed water volume = 1216 L
Feed water fluoride = 366 mg/L
Feed flowrate = 7.7 LPM (0.46 m3/hr)
Permeate flowrate = 6 LPM (0.36 m3/hr)
SBRO service duration = 15 mins, flushing duration 110 sec
Recovery = 78%

## Slide 6: Run 1 Feed water analysis
Sample | Feed solution
pH | 7.34
Conductivity (µS/cm) | 2310
Bicarbonate alkalinity | 28.0
Fluoride (mg/L) | 366
Chloride (mg/L) | 34.2
Phosphate (mg/L) | 10.7
Sulfate (mg/L) | 6.8
Nitrate (mg/L) | 153
Ammonium as NH4 (mg/L) | 17.5
Aluminium (mg/L) | 0.13
Boron (mg/L) | 2.85
Calcium (mg/L) | 0.47
Magnesium (mg/L) | <0.1
Iron as Fe (mg/L) | 0.126
Potassium (mg/L) | 5.178
Total Silica (mg/L) | 13.3
Sodium (mg/L) | 503
TOC (mg/L) | 18.5
TDS (mg/L) | 1136

## Slide 8
Feed tank
BW30 PRO-4040
High pressure pump
Booster pump
Cartridge filter
Notes: Taking video for the setup, membrane autopsy after the end of the run?

## Slide 9: Run 1 - SBRO Reject Conductivity Profile
Chart: Elapsed time
| 0 | 0 | 4.8611111111111494E-3 | 1.1805555555555569E-2 | 1.2500000000000011E-2 | 1.3194444444444453E-2 | 1.5277777777777779E-2 | 2.3611111111111083E-2 | 3.0555555555555614E-2 | 3.4027777777777768E-2 | 3.6111111111111149E-2 | 3.8194444444444475E-2 | 3.8888888888888917E-2 | 4.0972222222222243E-2 | 4.7222222222222276E-2 | 5.1388888888888928E-2 | 5.4861111111111083E-2 | 5.555555555555558E-2 | 5.9722222222222232E-2 | 6.6666666666666763E-2 | 7.0138888888888862E-2 | 7.3611111111111183E-2 | 7.7083333333333393E-2 | 8.4722222222222254E-2
 | 3489 | 6146 | 7540 | 5340 | 5200 | 3489 | 7645 | 8065 | 8146 | 8095 | 5219 | 3429 | 4488 | 8254 | 8321 | 8351 | 4155 | 6637 | 7695 | 7767 | 4710 | 3820 | 8284

## Slide 10: Run 1 Permeate analysis
Sample | Results
pH | 6.46
Conductivity (µS/cm) | 82.4
Bicarbonate alkalinity | 0.8
Fluoride (mg/L) | 8
Chloride (mg/L) | 12.1
Phosphate (mg/L) | <1
Sulfate (mg/L) | 1.4
Nitrate (mg/L) | 15.9
Ammonium as NH4 (mg/L) | 3.3
Aluminium (mg/L) | <0.1
Boron (mg/L) | 0.53
Calcium (mg/L) | <0.1
Magnesium (mg/L) | <0.1
Iron (mg/L) | <0.1
Potassium (mg/L) | 0.422
Total Silica (mg/L) | <0.2
Sodium (mg/L) | 11.5
TOC (mg/L) | 3.1
TDS (mg/L) | 44

## Slide 11: Run 1 Reject analysis
Sample | Results
pH | 7.26
Conductivity (µS/cm) | 7380
Bicarbonate alkalinity | 129.6
Fluoride (mg/L) | 1307
Chloride (mg/L) | 64
Phosphate (mg/L) | 38
Sulfate (mg/L) | 21.3
Nitrate (mg/L) | 507
Ammonium as NH4 (mg/L) | 0.5
Aluminium (mg/L) | 0.22
Boron (mg/L) | 10.23
Calcium (mg/L) | 1.43
Magnesium (mg/L) | 0.175
Iron (mg/L) | 0.383
Potassium (mg/L) | 6.369
Total Silica (mg/L) | 52.0
Sodium (mg/L) | 1631
TOC (mg/L) | 57.0
TDS (mg/L) | 3976

## Slide 12: Summary
Initial F = 366 mg/L (>350 mg/L)
Recovery = 78% (>75%)
Effluent F = 8 mg/L (<10 mg/L)

## Slide 13: Schedule
Event | Description | Date
01 | Pilot Readiness | 25-Jan
02 | Sample Collection at Site | 18-Jan to 25-Jan 23 Jan – 2 Feb
03 | Micron/Exyte witness | 01-Feb – Exyte visit
04 | Pilot Operation | 02-Feb to 23-Feb
05 | Report Preparation | 09-Feb to 22-Feb
06 | Draft Submission Review | 23-Feb to 07-Mar
07 | Final Report Submission | 08-Mar to 15-Mar