## Slide 1
MICRON – HF WASTEWATER TREAMENT
SIMULATION & BENCH TESTING – Dec 2021
Siva Kumar Kota/Chun Yew
Hiep Le/Sankar
Part 1

## Slide 2
HFW Treatment Objectives
The objectives of simulation and bench testing are
  To identify the optimized flow scheme to treat HFW wastewater
  To compare the treatability of the HFW wastewater between Calcium hydroxide and Calcium chloride.
  To compare the quantity and quality of generated sludge
  To meet sludge quality >80% of CaF2
  To meet discharge F<10ppm and TDS <3000 ppm

## Slide 3: Simulation summary
Option 1 – NF90/270 + BWRO
Option 1a – NF270 + BWRO (Two Pass)
Option 2 – NF270 + SWRO (Single Pass)
Option 3– NF270 + SWRO (1st pass) + BWRO (2nd pass)
Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)
Option 5– NF270 followed by SWRO (clarified water recycle)
Option 5a– NF270 followed by SWRO (separate sludge)
Option 6– NF270 followed by SWRO (F-800 ppm)
Option 6a– NF270 followed by SWRO (F-800 ppm and combined sludge)
Option 6b– NF270 followed by SWRO (F-600 ppm)
Option 7- HFW Effluent treatment
Notes: 600 ppm max
350 ppm avg

## Slide 4
Micron 10X – Influent Wastewater quality
Parameters | Unit | HF Wastewater
TDS | mg/L | 698
pH | - | 3.6
TSS | mg/L | 96.0
NH4 | mg/L | 207
HCO3 | As CaCO3 mg/L | <20
CO3 | As CaCO3 mg/L | <20
NO3 | mg/L | 73.4
SO4 | mg/L | 174
K | mg/L | 2.92
Na | mg/L | 250
Mg | mg/L | 0.085
Ca | mg/L | 0.20
Sr | mg/L | 0.00041
Ba | mg/L | 0.0016
Cl | mg/L | 25.1
Parameters | Unit | HF Wastewater
F | mg/L | 1136
SiO2 | mg/L | 50.8
B | mg/L | 0.25
Al | mg/L | 0.068
Br | mg/L | 30.3
Cu | mg/L | 0.0028
Fe | mg/L | 0.065
Mn | mg/L | 0.0058
TOC | mg/L | 75.8
O&G | mg/L | <10
PO4 | mg/L | 12.3
COD | mg/L | 280
Total Hardness | As CaCO3 mg/L | 0.85
Total Alkalinity | As CaCO3 mg/L | <20

## Slide 5
Option1 - NF90/270 + BWRO
5
BWRO
NF
HF WW
Polishing Filters
Coagulation, Clarifier
sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
F: 105 m3/hr
F:404 mg/l
PO4: 0 mg/l
F: 90 m3/hr
F:30 mg/l
PO4: 0 mg/l
F: 61 m3/hr
F:3957 mg/l
PO4: 355,2 mg/l
F: 85 m3/hr
F:<10 mg/l
PO4: 0 mg/l
reject
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 6
Simulation summary
6
Performed different simulations/projections for the scheme UF, NF & RO scheme
UF:
  WW contains high amount of TSS (96 mg/l) and TOC (>50 mg/l).
  Achieved recovery ~84% at 41 LMH
NF & RO:
  Tried different types of membranes (tighter vs loose membrane)
  WW contains high amount of F (1136 mg/l) and Phosphate (100 mg/l).
  Tighter membrane:
    Phosphate rejection>99.5%
    Fluoride rejection~70%
  Loose membrane:
    Phosphate rejection>99.5%
    Fluoride rejection : 30-40%
  Overall system recovery ~72%
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 7: UF Projections
NF
RO

## Slide 8: NF & RO Projections
NF
RO

## Slide 9: NF & RO Projections Contd.,
NF – Tighter membrane
BWRO

## Slide 10: NF & RO Projections Contd.,
NF – Loose membrane
BWRO

## Slide 11
Option1a - NF270 + BWRO (Two Pass)
11
BWRO (2 pass)
NF270
HF WW
Treated Water
Polishing Filters
Coagulation, Clarifier
sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
reject
UF
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
SWRO – 1 PASS
BWRO -2 PASS
SWRO + BWRO
Treated water BWRO

## Slide 12: Option 1a – NF270 + BWRO (TWO Pass)

## Slide 13: Option 1a – NF270 + BWRO (TWO Pass)
NF 270– Loose membrane

## Slide 14: Option 1a – NF270 + BWRO (TWO Pass)
1st Pass BWRO
2nd Pass BWRO

## Slide 15
Option 2 - NF270 + SWRO (SINGLE Pass)
15
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 16: Option 2 – NF270 + SWRO (SINGLE Pass)

## Slide 17: Option 2 – NF270 + SWRO (SINGLE Pass)
NF270
SWRO

## Slide 18: Option 3– NF270 + SWRO (1st pass) + BWRO (2nd pass)
BWRO (2nd pass)
Chemical Parameters |  | 
Ammonia (as N) | mg/L | <1.0
Aluminium | mg/L | <0.1
Barium | mg/L | <0.1
Boron | mg/L | <0.5
Calcium | mg/L | <20
Chloride | mg/L | <20
Copper | mg/L | <0.05
Fluoride | mg/L | <0.5
Iron | mg/L | <0.04
Manganese | mg/L | <0.05
Nitrate (as N) | mg/L | <5
Sodium | mg/L | <20
Sulphate | mg/L | <5
Silica (as SiO2) | mg/L | <3
Strontium | mg/L | <0.1
Total Trihalomethanes Ratio | - | <0.04
Total Organic Carbon (TOC) | mg/L | <0.5
Total Hardness (as CaCO3) | mg/L | <50
Zinc | mg/L | <0.1
NEWater

## Slide 19: Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)

## Slide 20: Option 4– NF270 + SWRO (1st stage) + BWRO (2nd stage)
NF270
SWRO (1st stage) + BWRO (2nd stage)