## Slide 1
MICRON – HF WASTEWATER TREAMENT
SIMULATION & BENCH TESTING – Dec 2021
Siva Kumar Kota/Chun Yew
Hiep Le/Sankar
Part 2

## Slide 2
Option 5 -NF270 followed by SWRO (clarified water recycle)
2
SWRO
NF 270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations

## Slide 3: Option 5– NF270 followed by SWRO
NF270

## Slide 4: Option 5– SWRO (NF permeate and F rich clarified water)
SWRO

## Slide 5
Option 5a - NF270 followed by SWRO (separate sludge)
5
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
F:1136 mg/l
PO4: 100 mg/l
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM

## Slide 6: Option 5a – NF270 (Loose membrane)

## Slide 7: Option 5a – SWRO with pH adjustment

## Slide 8: NEWater spec
Chemical Parameters |  | 
Ammonia (as N) | mg/L | <1.0
Aluminium | mg/L | <0.1
Barium | mg/L | <0.1
Boron | mg/L | <0.5
Calcium | mg/L | <20
Chloride | mg/L | <20
Copper | mg/L | <0.05
Fluoride | mg/L | <0.5
Iron | mg/L | <0.04
Manganese | mg/L | <0.05
Nitrate (as N) | mg/L | <5
Sodium | mg/L | <20
Sulphate | mg/L | <5
Silica (as SiO2) | mg/L | <3
Strontium | mg/L | <0.1
Total Trihalomethanes Ratio | - | <0.04
Total Organic Carbon (TOC) | mg/L | <0.5
Total Hardness (as CaCO3) | mg/L | <50
Zinc | mg/L | <0.1

## Slide 9: Option 5a – polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 10: Option 5a - NF270 Reject chemical precipitation using Ca(OH)2

## Slide 11: Option 5a- NF270 Reject chemical precipitation using Ca(OH)2

## Slide 12: Option 5a-SWRO Reject chemical precipitation

## Slide 13: Option 5a -SWRO Reject chemical precipitation

## Slide 14
Option 6 - NF270 followed by SWRO (F-800 ppm)
14
NF270
UF
HF WW
SWRO
Coagulation,Clarifier
Sludge
F: 150 m3/hr
F:800 mg/l
PO4: 100 mg/l
CoagulationClarifier
Sludge
BWRO (optional)
Stream 1
Stream 2
Stream 3
Stream 4
Stream 5
Stream 6
Stream 7
Stream 9
Stream 8
Stream 10
Stream 11
Polishing filters
Stream 12
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM
AMMONIUM PEROXIDE WASTE- H2O2
PETERG7@

## Slide 15: HFW – Feed Water Characteristics

## Slide 16: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 17: Option 6 – NF270 + SWRO With 800 ppm of F

## Slide 18: Option 6 – NF270+SWRO with 800 PPM of F
NF270
SWRO
Stream 4
Stream 9

## Slide 19: Option 6 – Polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 20: Option 6 – Polishing BWRO to meet NEWater
Notes: Cooling water spec
Ammonia<5ppm
Fluoride<2 ppm

## Slide 21: Option 6-NF270 Reject chemical precipitation using Ca(OH)2
Stream 6-sludge
Stream 419.3 m3/hr
Stream 518 m3/hr

## Slide 22: Option 6- NF270 Reject chemical precipitation using Ca(OH)2
>80% of CaF2 sludge

## Slide 23: Option 6- SWRO Reject chemical precipitation
Stream 11-sludge
Stream 915.8 m3/hr
Stream 1014.8 m3/hr

## Slide 24: Option 6 -SWRO Reject chemical precipitation
>80% of CaF2 sludge

## Slide 25
Option 6a – NF270 followed by SWRO (F-800 ppm and combined sludge)
25
NF270
UF
HF WW
SWRO
Sludge
F: 150 m3/hr
F:800 mg/l
PO4: 100 mg/l
CoagulationClarifier
BWRO (optional)
Stream 1
Stream 2
Stream 3
Stream 4
Stream 6
Stream 9
Stream 5
Stream 10
Stream 7
Stream 8
Polishing filters
Notes: NF/RO –projections
FBR –Reject treatment
Npv calculations
Ammonia -20 ppm
TOC-<5
FLUORIDE -800 PPM

## Slide 26: Option 6a–combined reject chemical precipitation –CaF2 sludge
Stream 7-sludge
Stream 4&535.3 m3/hr
Stream 633.5 m3/hr

## Slide 27: Option 6a–combined reject chemical precipitation –CaF2 sludge
>80% of CaF2 sludge

## Slide 28: Option 6b – NF270 + SWRO With 600 ppm of F

## Slide 29: Option 6b – NF270+SWRO WITH 600 PPM of F
NF270
SWRO

## Slide 30: Option 7-HFW Effluent treatment – UF, RO

## Slide 31: Option 7- HFW Effluent treatment ( UF & RO)

## Slide 32: Option 7- HFW Effluent treatment (UF& RO)
Pass 1 – BWRO
Pass 2 - BWRO