## Slide 1
MICRON – HF WASTEWATER TREAMENT
SIMULATION & BENCH TESTING – Dec 2021
Siva Kumar Kota/Chun Yew
Hiep Le/Sankar
Part 5

## Slide 2
Option 7 - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (separate sludge)
2
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water

## Slide 3: Option 7 - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (separate sludge)

## Slide 4: Option 7 - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (separate sludge)

## Slide 5: Option 7 - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (separate sludge)
NF270
SWRO

## Slide 6: Option 7- NF270 Separate Sludge
>80% CaF2

## Slide 7: Option 7- SWRO Separate Sludge
>80% CaF2

## Slide 8
Option 7a - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (Combined sludge)
8
SWRO
NF270
HF WW
Polishing Filters
Coagulation, Clarifier
Phosphate sludge
F: 150 m3/hr
Coagulation, Clarifier
CaF2 sludge
UF
Treated Water

## Slide 9: Option 7a - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (Combined sludge)

## Slide 10: Option 7a - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (Combined sludge)

## Slide 11: Option 7a - NF270 followed by SWRO with 800 ppm of F, ammonia -207 ppm (Combined sludge)
NF270
SWRO

## Slide 12: Option 7a- Combined Sludge
>80% CaF2