## Slide 1
MICRON – HF WASTEWATER TREAMENT
SIMULATION & BENCH TESTING – Dec 2021
Siva Kumar Kota/Chun Yew
Hiep Le/Sankar
Part 6

## Slide 2
Combined Sludge XRD analysis
2
Dosage: 6000 mg/l of lime and 4000 mg/l of CaCl2

## Slide 3
Combined Sludge XRD analysis
3
XRF Results shows that Calcium fluoride sludge as a major part (>80%)
Dosage: 6000 mg/l of lime and 4000 mg/l of CaCl2