## Slide 1: Pilot Study Review
Client: Exyte
Location: Singapore
Date : 20 Dec 2023

## Slide 2: Overall Process Description

## Slide 3: Objectives
Confirm water analysis of the raw samples
Confirm water analysis of the mixed sample
Confirm final brine quality
Check for any anomalies in water analysis such as high F, NO3, etc
Calculate the optimal mixing ratios
Calculate scaling potential
Calculate maximum recovery that can be achieved
Confirm ≥75% recovery
Confirm permeate water quality meets KPIs
Confirm operating pressures and flow rates

## Slide 4: Target Operation
Design Basis will be adjusted depending on the received water quality

## Slide 5: HFW and LSR sampling points – Run 1
Sampling points | Volume (L) | Total volume (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 48 | 100 | 10 | 1000 (1m3)
HFW Gravity Drain A2 | 48 |  |  | 
HFW Gravity Drain Chem Room | 2* |  |  | 
HFW Gravity Drain Corrosive gas room | 2* |  |  | 
LSR A2 |  |  |  | 
LSR A2 transfer pump | 100 | 100 | 10 | 1000 (1m3)
*Collect in two separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 6: HFW and LSR sampling points – Run 2
Sampling points | Volume (L) | Total volume (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 192 | 400 | 10 | 4000 (4m3)
HFW Gravity Drain A2 | 192 |  |  | 
HFW Gravity Drain Chem Room | 8* |  |  | 
HFW Gravity Drain Corrosive gas room | 8* |  |  | 
LSR A2 |  |  |  | 
LSR A2 transfer pump | 400 | 400 | 10 | 4000 (4m3)
*Collect in 8x separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 8: Sample analysis
Samples | Measured F (mg/L) 18 Aug | Volume (L) | Combined fluoride by calculation (mg/L)
HFW |  |  | 
HFW Gravity Drain A1 | 580 | 48 | 1076.6
HFW Gravity Drain A2 | 140 | 48 | 
HFW Chem Room | 30857 | 2 | 
HFW Corrosive Gas Room | 417 | 2 | 
LSR |  |  | 
LSR A2 | 29.4 | NA | NA

## Slide 9: Sample analysis
Samples | Measured F (mg/L) 18 Aug | Measured F (mg/L) 19 Aug, 6 am | Measured F (mg/L) 20 Aug, 6 pm | Measured F (mg/L) 21 Aug, 11 am
HFW Gravity Drain A1 | 580 | 454 | 422 | 
HFW Gravity Drain A2 | 140 |  |  | 
HFW Chem Room | 30,857 | 546 | 27,953 | 15,132
HFW Corrosive Gas Room | 417 | 422 | 540 | 407

## Slide 10: Alternative proposal
EQ tank 1
Provision to divert Chem drain (due to high fluoride) to Eq tank 1 whenever there is a surge of fluoride in Eq tank 3
When fluoride in Eq tank 3 is high, HFW line will stop and LSR A1 diversion will begin
*Open for discussion*

## Slide 11: Schedule
Items | Status | PO number | ETA
Membranes BW30 PRO-4040 | PO issued | POGIH22357 | 12 Jan
Pressure vessels | PO issued | POGIH22329 | 12 Jan
High pressure hose to upgrade existing setup | Pending delivery | COD | 10 Jan
Fittings | Procured and delivered | NA | NA

## Slide 12: Sampling Log

## Slide 13: Test Setup
Feed Tank
Micron filters (CF & ACF)
Membrane
Feed Pump
HP Pump
Control Panel
Pressure Gauge

## Slide 14: Membrane
Filmtec™ BW30 PRO-4040 PILOT
Active Area: 85 sqft (7.9 m2)
Permeate Flow: 2600 gpd
Min Rejection: 99.5%
Lenth: 40”
Diameter: 3.9”
Fortilife™ CR100-4040 PILOT
Active Area: 78 sqft (7.25 m2)
Permeate Flow: 2400 gpd
Min Rejection: 99.4%
Lenth: 40”
Diameter: 3.9”

## Slide 15: Test Run
Run 1
  1-2 m3 of mixed LSR + HFW
  Continuous Semi-batch Operation
  3-6 hours within 1 day
  Feed Rate: 0.4 m3/hr
Run 2
  4-8 m3 of mixed LSR + HFW
  Daily Semi-batch Operation
  3-6 hours daily for 4 days
  Feed Rate: 0.4 m3/hr

## Slide 16: Data Collected
ROI Feed Pressure over Time
ROI Effluent Conductivity over Time
ROI Reject Concentration over time
Sample of Combined Effluent water
Sample of Combined Reject water

## Slide 17: Analysis
Design Basis will be updated accordingly to the test
Update RO Projection
Update Antiscalant Projection

## Slide 18: Schedule
Event | Description | Date
01 | Pilot Readiness | 25-Jan
02 | Sample Collection at Site | 18-Jan to 25-Jan
03 | Micron/Exyte witness | 01-Feb
04 | Pilot Operation | 26-Jan to 08-Feb
05 | Report Preparation | 09-Feb to 22-Feb
06 | Draft Submission Review | 23-Feb to 07-Mar
07 | Final Report Submission | 08-Mar to 15-Mar