## Slide 1: Pilot Study Update
Client: Exyte
Location: Singapore
Date : 17 Jan 2024

## Slide 2: Discussion points
Sample collection starts 18 Jan 24
Do we need Micron/Exyte witness for sample collection?

## Slide 3: HFW and LSR sampling points – Run 1
Sampling points | Volume (L) | Total volume (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 70 | 100 | 10 | 1000 (1m3)
HFW Gravity Drain A2 | 30 |  |  | 
HFW Gravity Drain Chem Room | 2* |  |  | 
HFW Gravity Drain Corrosive gas room | 2* |  |  | 
LSR A2 |  |  |  | 
LSR A2 transfer pump | 100 | 100 | 10 | 1000 (1m3)
Ratio HFW A1: A2= 7:3
*Collect in two separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 4: HFW and LSR sampling points – Run 2
Sampling points | Volume (L) | Total volume (L) | Frequency per week | Total quantity per week (L)
HFW |  |  |  | 
HFW Gravity Drain A1 | 268 | 400 | 10 | 4000 (4m3)
HFW Gravity Drain A2 | 116 |  |  | 
HFW Gravity Drain Chem Room | 8* |  |  | 
HFW Gravity Drain Corrosive gas room | 8* |  |  | 
LSR A2 |  |  |  | 
LSR A2 transfer pump | 400 | 400 | 10 | 4000 (4m3)
*Collect in 8x separate 20 L carboys and mixing will be done in GIH lab, LSR A1 feed is not required
Sample to be collected once per 12-hour shift

## Slide 5: Sample analysis
Samples | Measured F (mg/L) 18 Aug | Volume (L) | Combined fluoride by calculation (mg/L)
HFW |  |  | 
HFW Gravity Drain A1 | 580 | 48 | 1076.6
HFW Gravity Drain A2 | 140 | 48 | 
HFW Chem Room | 30857 | 2 | 
HFW Corrosive Gas Room | 417 | 2 | 
LSR |  |  | 
LSR A2 | 29.4 | NA | NA

## Slide 6: Sample analysis
Samples | Measured F (mg/L) 18 Aug | Measured F (mg/L) 19 Aug, 6 am | Measured F (mg/L) 20 Aug, 6 pm | Measured F (mg/L) 21 Aug, 11 am | Measured F (mg/L) 9 Jan 24, 1:30 pm
HFW Gravity Drain A1 | 580 | 454 | 422 | 1015 | 592
HFW Gravity Drain A2 | 140 | 735 | 473 | 463 | 351
HFW Chem Room | 30,857 | 546 | 27,953 | 15,132 | 828
HFW Corrosive Gas Room | 417 | 422 | 540 | 407 | 162
HFW Combined Header to Eq tank |  |  |  |  | 395

## Slide 7: Schedule for lab setup
Items | Status | PO number | ETA
Membranes BW30 PRO-4040 | PO issued | POGIH22357 | Delivered today –10 Jan
Pressure vessels | PO issued | POGIH22329 | Delivered today -10 Jan
High pressure hose and pressure relieve valve to upgrade existing setup | Delivered | COD | 12 Jan
Fittings | Procured and delivered | NA | NA

## Slide 8: Schedule
Event | Description | Date
01 | Pilot Readiness | 25-Jan
02 | Sample Collection at Site | 18-Jan to 25-Jan
03 | Micron/Exyte witness | 01-Feb
04 | Pilot Operation | 26-Jan to 08-Feb
05 | Report Preparation | 09-Feb to 22-Feb
06 | Draft Submission Review | 23-Feb to 07-Mar
07 | Final Report Submission | 08-Mar to 15-Mar