## Slide 1: Micron US ID1 Project
2 Aug 2023
Angela

## Slide 2: Objective & Design Basis
To remove H2O2 using FBO from 70 ppm to not detectable
To reduce the feed COD from 50 to 30 mg/L
56 m3 Tank
56 m3 Tank
211 m3/h
211 m3/h

## Slide 3: Assumptions & Calculations
H2O2 + O3 → H2O + 2O2
70 mg/L H2O2 = 2.06 mmol/L equals to 99 mg/L ozone
Assume retention time 15 min, and 1 LPM 11% w.t. (153 g/Nm3) ozone per 100L
100 L/15 min = 0.4 m3/h 211 m3/h is 528 times
1 LPM x 153 g/Nm3 x 528 = 4.8 kg/h ozone with concentration >= 11% w.t. or 153 g/Nm3
4.8 kg/h / 153 g/Nm3 = 31 m3/h, 5 pcs of MicroGas FS752DC

## Slide 4: Summary
Device | Qty
Ozone Generator 4.8 kg/h with ozone concentration >= 11% w.t. or 153 g/Nm3 | 2 sets (1 set per tank)
MicroStar Nano Bubbler FS752DC | 10 pcs (5 pcs per tank)
Pump & Piping etc. |